## Sheet1 (hidden)
panels | Type of load | Normal homeRun Tray (Right Part)
|  | Cable | D Cable | R Cable | C.Sa Cable | NO.OF Cable | Total C.Sa
normal -LPPG2(Ground floor ) | Lighting | 3*3 mm^2 | 11.6 | 5.8 |  |  | 0
| Sockets | 3*3 mm^2 | 11.6 | 5.8 |  |  | 0
| Hand dryer | 3*4 mm^2 | 12.3 | 6.15 |  |  | 0
| F.C.U | 3*4 mm^2 | 12.3 | 6.15 |  |  | 0
sum of C.Sa | [6 empty] | 0
F.R | [6 empty] | 0.4
Area of Tray | [6 empty] | 0
Area of Tray with 25% Spare | [6 empty] | 0
Height
Width
dimantion of Tray

## Sheet1 (2)
Panel Name | Fed From | No. OF RUNS | CONDUCTOR | CORES | INSULATION | CSA | EARTH NO. OF RUNS | EARTH CSA
NLP-B | MDB | 1 | CU | MULTI CORE | PVC/PVC | 4Cx4 mm2 | 1 | 1x4
NSP-B | MDB | 1 | CU | MULTI CORE | PVC/PVC | 3Cx35+16 mm2 | 1 | 1x16
NSP2-B | MDB | 1 | CU | MULTI CORE | PVC/PVC | 3Cx95+50 mm2 | 1 | 1x50
EMDB | MDB | 1 | CU | MULTI CORE | PVC/PVC | 3Cx95+50 mm2 | 1 | 1x50
UPS | EMDB | 1 | CU | MULTI CORE | PVC/PVC | 4Cx10 mm2 | 1 | 1x10
CLP-B | UPS | 1 | CU | MULTI CORE | PVC/PVC | 4Cx4 mm2 | 1 | 1x4
CSP-B | UPS | 1 | CU | MULTI CORE | PVC/PVC | 4Cx6 mm2 | 1 | 1x6

## MDB
CABLE TRAY SIZING
CABLE TRAY TAG | Layer | FROM | TO | Tag | CABLE SIZE | D-CABLE | NO.OF CABLE | WIDTH | CABLE TRAY SIZE
SEC1 | LAYER1 | MDB | NLP-B | C1 | 4X4 MM2-CU/PVC/PVC+1X4 MM2 G/CABLE TRAY | 19.7 | 1 | 361 | 400x50x1.5mm2
|  | MDB | NSP-B | C2 | (3X35+1X16) MM2-CU/PVC/PVC+1X16 MM2 G/CABLE TRAY | 28.7 | 1
|  | MDB | NSP2-B | C3 | (3X95+1X50) MM2-CU/PVC/PVC+1X50 MM2 G/CABLE TRAY | 42.6 | 1
|  | MDB | EMDP | C4 | (3X95+1X50) MM2-CU/PVC/PVC+1X50 MM2 G/CABLE TRAY | 42.6 | 1
sec2 | Layer1 | MDB | NLP-B | C1 | 4X4 MM2-CU/PVC/PVC+1X4 MM2 G/CABLE TRAY | 19.7 | 1 | 74.625 | 100x50x1.5mm2
sec3 | Layer1 | MDB | NSP-B | C2 | (3X35+1X16) MM2-CU/PVC/PVC+1X16 MM2 G/CABLE TRAY | 28.7 | 1 | 293.4375 | 300x50x1.5mm2
|  | MDB | NSP2-B | C3 | (3X95+1X50) MM2-CU/PVC/PVC+1X50 MM2 G/CABLE TRAY | 42.6 | 1
|  | MDB | EMDP | C4 | (3X95+1X50) MM2-CU/PVC/PVC+1X50 MM2 G/CABLE TRAY | 42.6 | 1
sec4 | Layer1 | MDB | NSP-B | C2 | (3X35+1X16) MM2-CU/PVC/PVC+1X16 MM2 G/CABLE TRAY | 28.7 | 1 | 71.75 | 100x50x1.5mm2
sec5 | LAYER1 | MDB | NSP2-B | C3 | (3X95+1X50) MM2-CU/PVC/PVC+1X50 MM2 G/CABLE TRAY | 42.6 | 1 | 213 | 200x50x1.5mm2
|  | MDB | EMDP | C4 | (3X95+1X50) MM2-CU/PVC/PVC+1X50 MM2 G/CABLE TRAY | 42.6 | 1
SEC6 | LAYER1 | MDB | NSP2-B | C3 | (3X95+1X50) MM2-CU/PVC/PVC+1X50 MM2 G/CABLE TRAY | 42.6 | 1 | 106.5 | 100x50x1.5mm2
SEC7 | LAYER1 | MDB | EMDP | C4 | (3X95+1X50) MM2-CU/PVC/PVC+1X50 MM2 G/CABLE TRAY | 42.6 | 1 | 106.5 | 100x50x1.5mm2
| LOAD NO. | CABLE DESCRIBTION | Panel Name | Fed From | No. OF RUNS | CONDUCTOR | CORES | INSULATION | CSA
| 1 | 4X4 MM2-CU/PVC/PVC+1X4 MM2 G/CABLE TRAY | NLP-B | MDB | 1 | CU | MULTI CORE | PVC/PVC | 4Cx4 mm2
| 2 | (3X35+1X16) MM2-CU/PVC/PVC+1X16 MM2 G/CABLE TRAY | NSP-B | MDB | 1 | CU | MULTI CORE | PVC/PVC | 3Cx35+16 mm2
| 3 | (3X95+1X50) MM2-CU/PVC/PVC+1X50 MM2 G/CABLE TRAY | NSP2-B | MDB | 1 | CU | MULTI CORE | PVC/PVC | 3Cx95+50 mm2
| 4 | (3X95+1X50) MM2-CU/PVC/PVC+1X50 MM2 G/CABLE TRAY | EMDB | MDB | 1 | CU | MULTI CORE | PVC/PVC | 3Cx95+50 mm2
| 5 | ((4X10MM2+(1X10 MM2) CU/PVC/PVC | UPS | EMDB | 1 | CU | MULTI CORE | PVC/PVC | 4Cx10 mm2
| 6 | ((4X4MM2+(1X4 MM2) CU/PVC/PVC | CLP-B | UPS | 1 | CU | MULTI CORE | PVC/PVC | 4Cx4 mm2
| 7 | ((4X6MM2)+(1X6 MM2) CU/PVC/PVC | CSP-B | UPS | 1 | CU | MULTI CORE | PVC/PVC | 4Cx6 mm2

## EMDP)
CABLE TRAY SIZING
CABLE TRAY TAG | Layer | FROM | TO | Tag | CABLE SIZE | D-CABLE | NO.OF CABLE | WIDTH | CABLE TRAY SIZE
SEC1 | LAYER1 | EMDP | UPS | C1 | ((4X10MM2+(1X10 MM2) CU/PVC/PVC | 22.1 | 1 | 44.2 | 50x50x2mm2
| LOAD NO. | CABLE DESCRIBTION | Panel Name | Fed From | No. OF RUNS | CONDUCTOR | CORES | INSULATION | CSA
| 1 | 4X4 MM2-CU/PVC/PVC+1X4 MM2 G/CABLE TRAY | NLP-B | MDB | 1 | CU | MULTI CORE | PVC/PVC | 4Cx4 mm2
| 2 | (3X35+1X16) MM2-CU/PVC/PVC+1X16 MM2 G/CABLE TRAY | NSP-B | MDB | 1 | CU | MULTI CORE | PVC/PVC | 3Cx35+16 mm2
| 3 | (3X95+1X50) MM2-CU/PVC/PVC+1X50 MM2 G/CABLE TRAY | NSP2-B | MDB | 1 | CU | MULTI CORE | PVC/PVC | 3Cx95+50 mm2
| 4 | (3X95+1X50) MM2-CU/PVC/PVC+1X50 MM2 G/CABLE TRAY | EMDB | MDB | 1 | CU | MULTI CORE | PVC/PVC | 3Cx95+50 mm2
| 5 | ((4X10MM2+(1X10 MM2) CU/PVC/PVC | UPS | EMDB | 1 | CU | MULTI CORE | PVC/PVC | 4Cx10 mm2
| 6 | ((4X4MM2+(1X4 MM2) CU/PVC/PVC | CLP-B | UPS | 1 | CU | MULTI CORE | PVC/PVC | 4Cx4 mm2
| 7 | ((4X6MM2)+(1X6 MM2) CU/PVC/PVC | CSP-B | UPS | 1 | CU | MULTI CORE | PVC/PVC | 4Cx6 mm2

## UPS
CABLE TRAY SIZING
CABLE TRAY TAG | Layer | FROM | TO | Tag | CABLE SIZE | D-CABLE | NO.OF CABLE | WIDTH | CABLE TRAY SIZE
SEC1 | LAYER1 | UPS | CLP-B | C1 | ((4X4MM2+(1X4 MM2) CU/PVC/PVC | 16 | 19.7 | 114.9375 | 150x50x2mm2
|  | UPS | CSP-B | C2 | ((4X6MM2)+(1X6 MM2) CU/PVC/PVC | 16 | 20.9
sec2 | Layer1 | UPS | CLP-B | C1 | ((4X4MM2+(1X4 MM2) CU/PVC/PVC | 16 | 19.7 | 74.625 | 100x50x1.5mm2
sec3 | Layer1 | UPS | CSP-B | C2 | ((4X6MM2)+(1X6 MM2) CU/PVC/PVC | 16 | 20.9 | 76.125 | 100x50x1.5mm2
| LOAD NO. | CABLE DESCRIBTION | Panel Name | Fed From | No. OF RUNS | CONDUCTOR | CORES | INSULATION | CSA
| 1 | 4X4 MM2-CU/PVC/PVC+1X4 MM2 G/CABLE TRAY | NLP-B | MDB | 1 | CU | MULTI CORE | PVC/PVC | 4Cx4 mm2
| 2 | (3X35+1X16) MM2-CU/PVC/PVC+1X16 MM2 G/CABLE TRAY | NSP-B | MDB | 1 | CU | MULTI CORE | PVC/PVC | 3Cx35+16 mm2
| 3 | (3X95+1X50) MM2-CU/PVC/PVC+1X50 MM2 G/CABLE TRAY | NSP2-B | MDB | 1 | CU | MULTI CORE | PVC/PVC | 3Cx95+50 mm2
| 4 | (3X95+1X50) MM2-CU/PVC/PVC+1X50 MM2 G/CABLE TRAY | EMDB | MDB | 1 | CU | MULTI CORE | PVC/PVC | 3Cx95+50 mm2
| 5 | ((4X10MM2+(1X10 MM2) CU/PVC/PVC | UPS | EMDB | 1 | CU | MULTI CORE | PVC/PVC | 4Cx10 mm2
| 6 | ((4X4MM2+(1X4 MM2) CU/PVC/PVC | CLP-B | UPS | 1 | CU | MULTI CORE | PVC/PVC | 4Cx4 mm2
| 7 | ((4X6MM2)+(1X6 MM2) CU/PVC/PVC | CSP-B | UPS | 1 | CU | MULTI CORE | PVC/PVC | 4Cx6 mm2