## NSP-B
Voltage drop calculation for DWG NO |  |  |  |  | CR05-05-EL-AD-10G | [6 empty] | filling calculation for DWG NO |  |  | M
voltage drop calculation | [11 empty] | filling ratio calculation
circuit |  | load |  |  |  | cable |  | results |  |  |  | circuit | c.s.a of cables |  |  |  |  | c.s.a of pipes | results
circuit no | conductor | load-VA | D.LOAD-VA | voltage-V | current-A | length-mt | R-ohm/km | %V.D | acceptance |  |  | no of cabe in pipe | OD-mm | A1-mm² | A2-mm² | A3-mm² | A(t)-mm² | conduit -mm² by inner diammeter | %fill ratio | acceptance
NSP-B | [11 empty] | LPPG2
1 | 3x3 mm2 | 2500 | 2250 | 220 | 10.2273 | 185.8 | 7.66 | 13.2325 | √ |  |  | 1 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
2 | 3x3 mm2 | 2000 | 1800 | 220 | 8.1818 | 167.8 | 7.66 | 9.5604 | √ |  |  | 2 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
3 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 140.6 | 7.66 | 6.008 | √ |  |  | 3 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
4 | 3x3 mm2 | 2000 | 1800 | 220 | 8.1818 | 171.8 | 7.66 | 9.7883 | √ |  |  | 4 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
5 | 3x3 mm2 | 0 | 0 | 220 | 0 | 101 | 7.66 | 0 | √ |  |  | 5 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
6 | 3x3 mm2 | 1250 | 1125 | 220 | 5.1136 | 119 | 7.66 | 4.2375 | √ |  |  | 6 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
7 | 3x3 mm2 | 1000 | 900 | 220 | 4.0909 | 103.4 | 7.66 | 2.9456 | √ |  |  | 7 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
8 | 3x3 mm2 | 1250 | 1125 | 220 | 5.1136 | 128 | 7.66 | 4.558 | √ |  |  | 8 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
9 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 105.6 | 7.66 | 4.5124 | √ |  |  | 9 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
11 | 3x3 mm2 | 1750 | 1575 | 220 | 7.1591 | -7 | 7.66 | -0.34897 | √ |  |  | 11 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
12 | 3x3 mm2 | 1000 | 900 | 220 | 4.0909 | 96.2 | 7.66 | 2.7405 | √ |  |  | 12 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
13 | 3x3 mm2 | 1750 | 1575 | 220 | 7.1591 | 68.4 | 7.66 | 3.41 | √ |  |  | 13 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
14 | 3x3 mm2 | 1750 | 1575 | 220 | 7.1591 | 197.2 | 7.66 | 9.8311 | √ |  |  | 14 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
15 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 193.2 | 7.66 | 8.2557 | √ |  |  | 15 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
16 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 181.6 | 7.66 | 7.76 | √ |  |  | 16 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
17 | 3x3 mm2 | 1250 | 1125 | 220 | 5.1136 | 183.6 | 7.66 | 6.5379 | √ |  |  | 17 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
18 | 3x3 mm2 | 1000 | 900 | 220 | 4.0909 | 193 | 7.66 | 5.4981 | √ |  |  | 18 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
19 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 174.4 | 7.66 | 7.4524 | √ |  |  | 19 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
20 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 139.6 | 7.66 | 5.9653 | √ |  |  | 20 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
21 | 3x3 mm2 | 1750 | 1575 | 220 | 7.1591 | 203.6 | 7.66 | 10.1501 | √ |  |  | 21 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
22 | 3x3 mm2 | 1250 | 1125 | 220 | 5.1136 | 70.2 | 7.66 | 2.4998 | √ |  |  | 22 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
23 | 3x3 mm2 | 1000 | 900 | 220 | 4.0909 | 210 | 7.66 | 5.9824 | √ |  |  | 23 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
24 | 3x3 mm2 | 1000 | 900 | 220 | 4.0909 | 37.4 | 7.66 | 1.0654 | √ |  |  | 24 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
25 | 3x3 mm2 | 1250 | 1125 | 220 | 5.1136 | 40.4 | 7.66 | 1.4386 | √ |  |  | 25 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
26 | 3x3 mm2 | 1000 | 900 | 220 | 4.0909 | 61 | 7.66 | 1.7377 | √ |  |  | 26 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
27 | 3x3 mm2 | 1250 | 1125 | 220 | 5.1136 | 76.4 | 7.66 | 2.7206 | √ |  |  | 27 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
28 | 3x3 mm2 | 1250 | 1125 | 220 | 5.1136 | 84.5 | 7.66 | 3.009 | √ |  |  | 28 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
29 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 88 | 7.66 | 3.7604 | √ |  |  | 29 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
30 | 3x3 mm2 | 750 | 675 | 220 | 3.0682 | 101.6 | 7.66 | 2.1708 | √ |  |  | 30 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
31 | 3x3 mm2 | 1750 | 1575 | 220 | 7.1591 | 70.8 | 7.66 | 3.5296 | √ |  |  | 31 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
32 | 3x3 mm2 | 500 | 450 | 220 | 2.0455 | 106.2 | 7.66 | 1.5127 | √ |  |  | 32 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
33 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 68.2 | 7.66 | 2.9143 | √ |  |  | 33 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
34 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 112.6 | 7.66 | 4.8116 | √ |  |  | 34 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
35 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 118.6 | 7.66 | 5.0679 | √ |  |  | 35 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
36 | 3x3 mm2 | 1000 | 900 | 220 | 4.0909 | 67.6 | 7.66 | 1.9258 | √ |  |  | 36 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
37 | 3x3 mm2 | 1250 | 1125 | 220 | 5.1136 | 45.4 | 7.66 | 1.6167 | √ |  |  | 37 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
38 | 3x3 mm2 | 1750 | 1575 | 220 | 7.1591 | 64 | 7.66 | 3.1906 | √ |  |  | 38 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
39 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 212.2 | 7.66 | 9.0676 | √ |  |  | 39 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
40 | 3x3 mm2 | 1750 | 1575 | 220 | 7.1591 | 219.6 | 7.66 | 10.9478 | √ |  |  | 40 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
41 | 3x3 mm2 | 2000 | 1800 | 220 | 8.1818 | 228.2 | 7.66 | 13.0017 | √ |  |  | 41 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
42 | 3x3 mm2 | 1750 | 1575 | 220 | 7.1591 | 239.8 | 7.66 | 11.9548 | √ |  |  | 42 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
43 | 3x3 mm2 | 1750 | 1575 | 220 | 7.1591 | 87.2 | 7.66 | 4.3472 | √ |  |  | 43 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
44 | 3x3 mm2 | 1750 | 1575 | 220 | 7.1591 | 91.2 | 7.66 | 4.5466 | √ |  |  | 44 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
45 | 3x3 mm2 | 1250 | 1125 | 220 | 5.1136 | 52.2 | 7.66 | 1.8588 | √ |  |  | 45 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
46 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 74 | 7.66 | 3.1621 | √ |  |  | 46 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
47 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 81.6 | 7.66 | 3.4869 | √ |  |  | 47 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
48 | 3x3 mm2 | 2000 | 1800 | 220 | 8.1818 | 116.6 | 7.66 | 6.6433 | √ |  |  | 48 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
49 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 133.8 | 7.66 | 5.7175 | √ |  |  | 49 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
50 | 3x3 mm2 | 1500 | 1350 | 220 | 6.1364 | 128.6 | 7.66 | 5.4953 | √ |  |  | 50 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
51 | 3x3 mm2 | 750 | 675 | 220 | 3.0682 | 114.6 | 7.66 | 2.4485 | √ |  |  | 51 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
52 | 3x3 mm2 | 2000 | 1800 | 220 | 8.1818 | 105.8 | 7.66 | 6.028 | √ |  |  | 52 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
53 | 3x3 mm2 | 1000 | 900 | 220 | 4.0909 | 73.8 | 7.66 | 2.1024 | √ |  |  | 53 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
54 | 3x3 mm2 | 1250 | 1125 | 220 | 5.1136 | 201.4 | 7.66 | 7.1718 | √ |  |  | 54 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
55 | 3x3 mm2 | 1250 | 1125 | 221 | 5.0905 | 217 | 7.66 | 7.6575 | √ |  |  | 55 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
57 | 3x3 mm2 | 1000 | 900 | 222 | 4.0541 | 127 | 7.66 | 3.553 | √ |  |  | 57 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
58 | 3x3 mm2 | 1750 | 1575 | 223 | 7.0628 | 125.4 | 7.66 | 6.0845 | √ |  |  | 58 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
59 | 3x3 mm2 | 500 | 450 | 224 | 2.0089 | 150.2 | 7.66 | 2.0637 | √ |  |  | 59 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
60 | 3x3 mm2 | 750 | 675 | 225 | 3 | 128.2 | 7.66 | 2.6187 | √ |  |  | 60 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
POWER ((NSP-B)) PANE;
|  |  | NO OF CIR | F1 | F2 |  |  | TOTAL
|  |  | 1 | 115 | 10 |  |  | 185.8
|  |  | 2 | 114 | 8 |  |  | 167.8
|  |  | 3 | 102 | 6 |  |  | 140.6
|  |  | 4 | 118 | 8 |  |  | 171.8 |  | F1 | LENGTH(in between + from panel)
|  |  | 5 | 108 | 0 |  |  | 101 |  | F2 | no of SOCKETS
|  |  | 6 | 88 | 5 |  |  | 119
|  |  | 7 | 80 | 4 |  |  | 103.4
|  |  | 8 | 97 | 5 |  |  | 128
|  |  | 9 | 67 | 6 |  |  | 105.6
|  |  | 11 | 0 | 0 |  |  | -7 |  |  | TOTAL WAT/200 | NO OF SOCKET
|  |  | 12 | 50 | 7 |  |  | 96.2 |  |  | 2000 | 10
|  |  | 13 | 45 | 4 |  |  | 68.4
|  |  | 14 | 151 | 7 |  |  | 197.2
|  |  | 15 | 147 | 7 |  |  | 193.2
|  |  | 16 | 143 | 6 |  |  | 181.6
|  |  | 17 | 145 | 6 |  |  | 183.6
|  |  | 18 | 162 | 5 |  |  | 193
|  |  | 19 | 151 | 4 |  |  | 174.4
|  |  | 20 | 101 | 6 |  |  | 139.6
|  |  | 21 | 165 | 6 |  |  | 203.6
|  |  | 22 | 24 | 7 |  |  | 70.2
|  |  | 23 | 179 | 5 |  |  | 210
|  |  | 24 | 14 | 4 |  |  | 37.4
|  |  | 25 | 17 | 4 |  |  | 40.4
|  |  | 26 | 30 | 5 |  |  | 61
|  |  | 27 | 53 | 4 |  |  | 76.4
|  |  | 28 | 53.5 | 5 |  |  | 84.5
|  |  | 29 | 57 | 5 |  |  | 88
|  |  | 30 | 63 | 6 |  |  | 101.6
|  |  | 31 | 55 | 3 |  |  | 70.8
|  |  | 32 | 60 | 7 |  |  | 106.2
|  |  | 33 | 60 | 2 |  |  | 68.2
|  |  | 34 | 74 | 6 |  |  | 112.6
|  |  | 35 | 80 | 6 |  |  | 118.6
|  |  | 36 | 29 | 6 |  |  | 67.6
|  |  | 37 | 22 | 4 |  |  | 45.4
|  |  | 38 | 33 | 5 |  |  | 64
|  |  | 39 | 166 | 7 |  |  | 212.2
|  |  | 40 | 181 | 6 |  |  | 219.6
|  |  | 41 | 182 | 7 |  |  | 228.2
|  |  | 42 | 186 | 8 |  |  | 239.8
|  |  | 43 | 41 | 7 |  |  | 87.2
|  |  | 44 | 45 | 7 |  |  | 91.2
|  |  | 45 | 6 | 7 |  |  | 52.2
|  |  | 46 | 43 | 5 |  |  | 74
|  |  | 47 | 43 | 6 |  |  | 81.6
|  |  | 48 | 78 | 6 |  |  | 116.6
|  |  | 49 | 80 | 8 |  |  | 133.8
|  |  | 50 | 90 | 6 |  |  | 128.6
|  |  | 51 | 76 | 6 |  |  | 114.6
|  |  | 52 | 90 | 3 |  |  | 105.8
|  |  | 53 | 20 | 8 |  |  | 73.8
|  |  | 54 | 178 | 4 |  |  | 201.4
|  |  | 55 | 186 | 5 |  |  | 217
|  |  | 57 | 96 | 5 |  |  | 127
|  |  | 58 | 102 | 4 |  |  | 125.4
|  |  | 59 | 104 | 7 |  |  | 150.2
|  |  | 60 | 120 | 2 |  |  | 128.2
total length from panel equal 250 m & average lenghth equal 20 m total length (in between and from panel) equal 630m & average 49 m
POWER(1)
[6 empty] | N | F1 | F2 | TOTAL(KW) | عدد الكشافات | LENGTH
[6 empty] | 1 | 4 | 6 | 2000 | 10 | 115
[6 empty] | 2 | 6 | 2 | 1600 | 8 | 114
[6 empty] | 3 | 2 | 4 | 1200 | 6 | 102
[6 empty] | 4 | 6 | 2 | 1600 | 8 | 118
[6 empty] | 5 |  |  | 0 | 0 | 108
[6 empty] | 6 | 5 |  | 1000 | 5 | 88
[6 empty] | 7 | 4 |  | 800 | 4 | 80
[6 empty] | 8 | 5 |  | 1000 | 5 | 97
[6 empty] | 9 |  | 6 | 1200 | 6 | 67
[6 empty] | 11 | 7 |  | 1400 | 7 | 50
[6 empty] | 12 | 1 | 3 | 800 | 4 | 45
[6 empty] | 13 | 7 |  | 1400 | 7 | 151
[6 empty] | 14 | 7 |  | 1400 | 7 | 147
[6 empty] | 15 | 1 | 5 | 1200 | 6 | 143
[6 empty] | 16 | 1 | 5 | 1200 | 6 | 145
[6 empty] | 17 |  | 5 | 1000 | 5 | 162
[6 empty] | 18 | 2 | 2 | 800 | 4 | 151
[6 empty] | 19 |  | 6 | 1200 | 6 | 101
[6 empty] | 20 | 4 | 2 | 1200 | 6 | 165
[6 empty] | 21 | 7 |  | 1400 | 7 | 24
[6 empty] | 22 | 1 | 4 | 1000 | 5 | 179
[6 empty] | 23 | 1 | 3 | 800 | 4 | 14
[6 empty] | 24 | 1 | 3 | 800 | 4 | 17
[6 empty] | 25 | 3 | 2 | 1000 | 5 | 30
[6 empty] | 26 | 1 | 3 | 800 | 4 | 53
[6 empty] | 27 |  | 5 | 1000 | 5 | 53.5
[6 empty] | 28 |  | 5 | 1000 | 5 | 57
[6 empty] | 29 | 2 | 4 | 1200 | 6 | 63
[6 empty] | 30 | 1 | 2 | 600 | 3 | 55
[6 empty] | 31 | 7 |  | 1400 | 7 | 60
[6 empty] | 32 | 2 |  | 400 | 2 | 60
[6 empty] | 33 | 4 | 2 | 1200 | 6 | 74
[6 empty] | 34 | 4 | 2 | 1200 | 6 | 80
[6 empty] | 35 | 2 | 4 | 1200 | 6 | 29
[6 empty] | 36 | 4 |  | 800 | 4 | 22
[6 empty] | 37 | 4 | 1 | 1000 | 5 | 33
[6 empty] | 38 | 6 | 1 | 1400 | 7 | 166
[6 empty] | 39 | 4 | 2 | 1200 | 6 | 181
[6 empty] | 40 | 7 |  | 1400 | 7 | 182
[6 empty] | 41 | 8 |  | 1600 | 8 | 186
[6 empty] | 42 | 7 |  | 1400 | 7 | 41
[6 empty] | 43 | 7 |  | 1400 | 7 | 45
[6 empty] | 44 | 6 | 1 | 1400 | 7 | 6
[6 empty] | 45 | 4 | 1 | 1000 | 5 | 43
[6 empty] | 46 | 4 | 2 | 1200 | 6 | 43
[6 empty] | 47 | 6 |  | 1200 | 6 | 78
[6 empty] | 48 | 6 | 2 | 1600 | 8 | 80
[6 empty] | 49 | 2 | 4 | 1200 | 6 | 90
[6 empty] | 50 | 4 | 2 | 1200 | 6 | 76
[6 empty] | 51 | 1 | 2 | 600 | 3 | 90
[6 empty] | 52 | 6 | 2 | 1600 | 8 | 20
[6 empty] | 53 | 2 | 2 | 800 | 4 | 178
[6 empty] | 54 | 1 | 4 | 1000 | 5 | 186
[6 empty] | 55 | 1 | 4 | 1000 | 5 | 96
[6 empty] | 57 | 4 |  | 800 | 4 | 102
[6 empty] | 58 | 4 | 3 | 1400 | 7 | 104
[6 empty] | 59 | 2 |  | 400 | 2 | 120
[6 empty] | 60 | 3 |  | 600 | 3 | 127
in case of single phase
%𝑉.𝐷=((2∗𝑅∗𝐼∗𝐿)∗100)/((𝑉)∗1000)→ ((<2%))
in case of single phase
in case of three phase
%𝑉.𝐷=((√3∗𝑅∗𝐼∗𝐿)∗100)/((𝑉)∗1000)→((<3%))
in case of three phase
A(t)=A1+A2+A3+... where : A1 -1 cable in pipe A2- 2 cable in pipe A3-3cable in pipe
A(T)= total C.S.A of cableinside pipe D=outside dimmeter of cable from catalogue
max occupancy ratio :1C=53%fill , 2C=31%fill 3C+=40%fill
𝐹.𝑅=(𝐶.𝑆.𝐴 𝑜𝑓 𝑐𝑎𝑏𝑙𝑒𝑠)/(𝐶.𝑆.𝐴 𝑜𝑓 𝑝𝑖𝑝𝑒)∗100=𝐴(𝑡)/(𝐶.𝑆.𝐴 𝑜𝑓 𝑝𝑖𝑝𝑒)((<53%→1𝐶<31%→2𝐶<40%→+3𝐶))
A(t)=A1+A2+A3+... 𝐴=(𝜋/4) 𝐷^(2 )=0.79𝐷^(2 ) where : A1 -1 cable in pipe A2- 2 cable in pipe A3-3cable in pipe
A(T)= total C.S.A of cableinside pipe D=outside dimmeter of cable from catalogue
max occupancy ratio :1C=53%fill , 2C=31%fill 3C+=40%fill

## NSP2-B
Voltage drop calculation for DWG NO |  |  |  |  | CR05-05-EL-AD-10G | [6 empty] | filling calculation for DWG NO |  |  | M
voltage drop calculation | [11 empty] | filling ratio calculation
circuit |  | load |  |  |  | cable |  | results |  |  |  | circuit | c.s.a of cables |  |  |  |  | c.s.a of pipes | results
circuit no | conductor | load-VA | D.LOAD-VA | voltage-V | current-A | length-mt | R-ohm/km | %V.D | acceptance |  |  | no of cabe in pipe | OD-mm | A1-mm² | A2-mm² | A3-mm² | A(t)-mm² | conduit -mm² by inner diammeter | %fill ratio | acceptance
NSP2-B | [11 empty] | LPPG2
1 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 105 | 7.66 | 11.1572 | √ |  |  | 1 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
2 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 123 | 7.66 | 13.0698 | √ |  |  | 2 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 353.81 | 30.0451 | √
3 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 124 | 7.66 | 13.1761 | √ |  |  | 3 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 354.81 | 29.9604 | √
4 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 132 | 7.66 | 14.0262 | √ |  |  | 4 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 355.81 | 29.8762 | √
5 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 152 | 7.66 | 16.1513 | √ |  |  | 5 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 356.81 | 29.7924 | √
6 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 160 | 7.66 | 17.0014 | √ |  |  | 6 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 357.81 | 29.7092 | √
7 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 176 | 7.66 | 18.7015 | √ |  |  | 7 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 358.81 | 29.6264 | √
8 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 173 | 7.66 | 18.3828 | √ |  |  | 8 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 359.81 | 29.544 | √
9 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 72 | 7.66 | 7.6506 | √ |  |  | 9 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 360.81 | 29.4622 | √
10 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 74 | 7.66 | 7.8631 | √ |  |  | 10 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 361.81 | 29.3807 | √
11 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 77 | 7.66 | 8.1819 | √ |  |  | 11 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 362.81 | 29.2997 | √
12 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 76 | 7.66 | 8.0757 | √ |  |  | 12 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 363.81 | 29.2192 | √
13 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 66 | 7.66 | 7.0131 | √ |  |  | 13 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 364.81 | 29.1391 | √
14 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 68 | 7.66 | 7.2256 | √ |  |  | 14 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 365.81 | 29.0595 | √
15 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 64 | 7.66 | 6.8006 | √ |  |  | 15 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 366.81 | 28.9802 | √
16 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 54 | 7.66 | 5.738 | √ |  |  | 16 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 367.81 | 28.9014 | √
17 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 30 | 7.66 | 3.1878 | √ |  |  | 17 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 368.81 | 28.8231 | √
18 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 27 | 7.66 | 2.869 | √ |  |  | 18 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 369.81 | 28.7451 | √
19 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 25 | 7.66 | 2.6565 | √ |  |  | 19 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 370.81 | 28.6676 | √
20 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 65 | 7.66 | 6.9068 | √ |  |  | 20 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 371.81 | 28.5905 | √
21 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 58 | 7.66 | 6.163 | √ |  |  | 21 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 372.81 | 28.5138 | √
22 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 55 | 7.66 | 5.8442 | √ |  |  | 22 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 373.81 | 28.4375 | √
23 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 58 | 7.66 | 6.163 | √ |  |  | 23 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 374.81 | 28.3617 | √
24 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 57 | 7.66 | 6.0567 | √ |  |  | 24 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 375.81 | 28.2862 | √
25 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 49 | 7.66 | 5.2067 | √ |  |  | 25 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 376.81 | 28.2111 | √
26 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 21 | 7.66 | 2.2314 | √ |  |  | 26 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 377.81 | 28.1365 | √
27 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 33 | 7.66 | 3.5065 | √ |  |  | 27 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 378.81 | 28.0622 | √
28 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 29 | 7.66 | 3.0815 | √ |  |  | 28 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 379.81 | 27.9883 | √
29 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 83 | 7.66 | 8.8195 | √ |  |  | 29 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 380.81 | 27.9148 | √
30 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 105 | 7.66 | 11.1572 | √ |  |  | 30 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 381.81 | 27.8417 | √
31 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 90 | 7.66 | 9.5633 | √ |  |  | 31 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 382.81 | 27.769 | √
32 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 87 | 7.66 | 9.2445 | √ |  |  | 32 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 383.81 | 27.6966 | √
33 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 87 | 7.66 | 9.2445 | √ |  |  | 33 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 384.81 | 27.6246 | √
34 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 97 | 7.66 | 10.3071 | √ |  |  | 34 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 385.81 | 27.553 | √
35 | 3x4 mm2 | 3730 | 3357 | 220 | 15.2591 | 102 | 7.66 | 10.8384 | √ |  |  | 35 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 386.81 | 27.4818 | √
38 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 103 | 7.66 | 4.4013 | √ |  |  | 38 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 387.81 | 27.4109 | √
39 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 91 | 7.66 | 3.8886 | √ |  |  | 39 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 388.81 | 27.3404 | √
40 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 85 | 7.66 | 3.6322 | √ |  |  | 40 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 389.81 | 27.2703 | √
41 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 19 | 7.66 | 0.8119 | √ |  |  | 41 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 390.81 | 27.2005 | √
42 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 25 | 7.66 | 1.0683 | √ |  |  | 42 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 391.81 | 27.1311 | √
43 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 29 | 7.66 | 1.2392 | √ |  |  | 43 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 392.81 | 27.062 | √
44 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 34 | 7.66 | 1.4529 | √ |  |  | 44 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 393.81 | 26.9933 | √
45 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 40 | 7.66 | 1.7093 | √ |  |  | 45 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 394.81 | 26.925 | √
46 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 46 | 7.66 | 1.9656 | √ |  |  | 46 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 395.81 | 26.8569 | √
47 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 47 | 7.66 | 2.0084 | √ |  |  | 47 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 396.81 | 26.7892 | √
48 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 32 | 7.66 | 1.3674 | √ |  |  | 48 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 397.81 | 26.7219 | √
49 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 135 | 7.66 | 5.7687 | √ |  |  | 49 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 398.81 | 26.6549 | √
50 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 132 | 7.66 | 5.6405 | √ |  |  | 50 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 399.81 | 26.5882 | √
51 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 41 | 7.66 | 1.752 | √ |  |  | 51 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 400.81 | 26.5219 | √
52 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 52 | 7.66 | 2.222 | √ |  |  | 52 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 401.81 | 26.4559 | √
53 | 3x4 mm2 | 6000 | 5400 | 220 | 24.5455 | 113 | 7.66 | 19.3146 | √ |  |  | 53 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 402.81 | 26.3902 | √
54 | 3x4 mm2 | 6000 | 5400 | 220 | 24.5455 | 57 | 7.66 | 9.7428 | √ |  |  | 54 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 403.81 | 26.3249 | √
[13 empty] | 5 | 3730
[13 empty] | 5 | 3730
[13 empty] | 4 | 3730
[13 empty] | 4 | 3730
[13 empty] | 1.5 | 3730
[13 empty] | 1.5 | 3730
[13 empty] | 4 | 3730
[13 empty] | 4 | 3730
[13 empty] | 1.5 | 3730
[13 empty] | 1.5 | 3730
[13 empty] | 1.5 | 3730
[13 empty] | 1.5 | 3730
[13 empty] | 1.5 | 3730
[13 empty] | 1.5 | 3730
[13 empty] | 1.5 | 3730
[13 empty] | 1.5 | 3730
[13 empty] | 5 | 3730
[13 empty] | 5 | 3730
[13 empty] | 5 | 3730
[13 empty] | 1.5 | 3730
|  |  | POWER | [9 empty] | 1.5 | 3730
[13 empty] | 1.5 | 3730
[13 empty] | 1.5 | 3730
|  |  | NO OF CIR | F1 | F2 |  |  | TOTAL |  |  |  |  | 1.5 | 3730
|  |  | 1 | 103 | 1 |  |  | 105 |  |  |  |  | 1.5 | 3730
|  |  | 2 | 121 | 1 |  |  | 123 |  |  |  |  | 1.5 | 3730
|  |  | 3 | 122 | 1 |  |  | 124 |  | F1 | LENGTH(in between + from panel) |  | 1.5 | 3730
|  |  | 4 | 130 | 1 |  |  | 132 |  | F2 | no of SOCKETS |  | 4 | 3730
|  |  | 5 | 150 | 1 |  |  | 152 |  |  |  |  | 4 | 3730
|  |  | 6 | 158 | 1 |  |  | 160 |  |  |  |  | 4 | 3730
|  |  | 7 | 174 | 1 |  |  | 176 |  |  |  |  | 4 | 3730
|  |  | 8 | 171 | 1 |  |  | 173 |  |  |  |  | 4 | 3730
|  |  | 9 | 70 | 1 |  |  | 72 |  |  |  |  | 4 | 3730
|  |  | 10 | 72 | 1 |  |  | 74 |  |  |  |  | 3 | 3730
|  |  | 11 | 75 | 1 |  |  | 77 |  |  |  |  | 3 | 3730
|  |  | 12 | 74 | 1 |  |  | 76 | [5 empty] | 1500
|  |  | 13 | 64 | 1 |  |  | 66 | [5 empty] | 1500
|  |  | 14 | 66 | 1 |  |  | 68 | [5 empty] | 1500
|  |  | 15 | 62 | 1 |  |  | 64 | [5 empty] | 1500
|  |  | 16 | 52 | 1 |  |  | 54 | [5 empty] | 1500
|  |  | 17 | 28 | 1 |  |  | 30 | [5 empty] | 1500
|  |  | 18 | 25 | 1 |  |  | 27 | [5 empty] | 1500
|  |  | 19 | 23 | 1 |  |  | 25 | [5 empty] | 1500
|  |  | 20 | 63 | 1 |  |  | 65 | [5 empty] | 1500
|  |  | 21 | 56 | 1 |  |  | 58 | [5 empty] | 1500
|  |  | 22 | 53 | 1 |  |  | 55 | [5 empty] | 1500
|  |  | 23 | 56 | 1 |  |  | 58 | [5 empty] | 1500
|  |  | 24 | 55 | 1 |  |  | 57 | [5 empty] | 1500
|  |  | 25 | 47 | 1 |  |  | 49 | [5 empty] | 1500
|  |  | 26 | 19 | 1 |  |  | 21 | [5 empty] | 1500
|  |  | 27 | 31 | 1 |  |  | 33
|  |  | 28 | 27 | 1 |  |  | 29
|  |  | 29 | 81 | 1 |  |  | 83
|  |  | 30 | 103 | 1 |  |  | 105
|  |  | 31 | 88 | 1 |  |  | 90
|  |  | 32 | 85 | 1 |  |  | 87
|  |  | 33 | 85 | 1 |  |  | 87
|  |  | 34 | 95 | 1 |  |  | 97
|  |  | 35 | 100 | 1 |  |  | 102
|  |  | 38 | 101 | 1 |  |  | 103
|  |  | 39 | 89 | 1 |  |  | 91
|  |  | 40 | 83 | 1 |  |  | 85
|  |  | 41 | 17 | 1 |  |  | 19
|  |  | 42 | 23 | 1 |  |  | 25
|  |  | 43 | 27 | 1 |  |  | 29
|  |  | 44 | 32 | 1 |  |  | 34
|  |  | 45 | 38 | 1 |  |  | 40
|  |  | 46 | 44 | 1 |  |  | 46
|  |  | 47 | 45 | 1 |  |  | 47
|  |  | 48 | 30 | 1 |  |  | 32
|  |  | 49 | 133 | 1 |  |  | 135
|  |  | 50 | 130 | 1 |  |  | 132
|  |  | 51 | 39 | 1 |  |  | 41
|  |  | 52 | 50 | 1 |  |  | 52
|  |  | 53 |  | 1
|  |  | 54 |  | 1
|  |  | 55 |  | 1
|  |  | 56 |  | 1
|  |  | 57 |  | 1
|  |  | 58 |  | 1
total length from panel equal 250 m & average lenghth equal 20 m total length (in between and from panel) equal 630m & average 49 m
in case of single phase
%𝑉.𝐷=((2∗𝑅∗𝐼∗𝐿)∗100)/((𝑉)∗1000)→ ((<2%))
in case of single phase
in case of three phase
%𝑉.𝐷=((√3∗𝑅∗𝐼∗𝐿)∗100)/((𝑉)∗1000)→((<3%))
in case of three phase
A(t)=A1+A2+A3+... where : A1 -1 cable in pipe A2- 2 cable in pipe A3-3cable in pipe
A(T)= total C.S.A of cableinside pipe D=outside dimmeter of cable from catalogue
max occupancy ratio :1C=53%fill , 2C=31%fill 3C+=40%fill
𝐹.𝑅=(𝐶.𝑆.𝐴 𝑜𝑓 𝑐𝑎𝑏𝑙𝑒𝑠)/(𝐶.𝑆.𝐴 𝑜𝑓 𝑝𝑖𝑝𝑒)∗100=𝐴(𝑡)/(𝐶.𝑆.𝐴 𝑜𝑓 𝑝𝑖𝑝𝑒)((<53%→1𝐶<31%→2𝐶<40%→+3𝐶))
A(t)=A1+A2+A3+... 𝐴=(𝜋/4) 𝐷^(2 )=0.79𝐷^(2 ) where : A1 -1 cable in pipe A2- 2 cable in pipe A3-3cable in pipe
A(T)= total C.S.A of cableinside pipe D=outside dimmeter of cable from catalogue
max occupancy ratio :1C=53%fill , 2C=31%fill 3C+=40%fill

## CSP-B
Voltage drop calculation for DWG NO |  |  |  |  | CR05-05-EL-AD-10G | [6 empty] | filling calculation for DWG NO |  |  | M
voltage drop calculation | [11 empty] | filling ratio calculation
circuit |  | load |  |  |  | cable |  | results |  |  |  | circuit | c.s.a of cables |  |  |  |  | c.s.a of pipes | results
circuit no | conductor | load-VA | D.LOAD-VA | voltage-V | current-A | length-mt | R-ohm/km | %V.D | acceptance |  |  | no of cabe in pipe | OD-mm | A1-mm² | A2-mm² | A3-mm² | A(t)-mm² | conduit -mm² by inner diammeter | %fill ratio | acceptance
CSP-B | [11 empty] | LPPG2
1 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 99 | 7.66 | 4.2304 | √ |  |  | 1 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
2 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 94 | 7.66 | 4.0168 | √ |  |  | 2 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
3 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 108 | 7.66 | 4.615 | √ |  |  | 3 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
4 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 114 | 7.66 | 4.8714 | √ |  |  | 4 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
5 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 116 | 7.66 | 4.9568 | √ |  |  | 5 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
6 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 123 | 7.66 | 5.256 | √ |  |  | 6 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
7 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 89 | 7.66 | 3.8031 | √ |  |  | 7 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
8 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 94 | 7.66 | 4.0168 | √ |  |  | 8 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
9 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 149 | 7.66 | 6.367 | √ |  |  | 9 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
10 | 3x4 mm2 | 1500 | 1350 | 220 | 6.1364 | 155 | 7.66 | 6.6234 | √ |  |  | 10 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
11 | 3x4 mm2 | 800 | 720 | 220 | 3.2727 | 4 | 7.66 | 0.09116 | √ |  |  | 11 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
12 | 3x4 mm2 | 1000 | 900 | 220 | 4.0909 | 5 | 7.66 | 0.14244 | √ |  |  | 12 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
13 | 3x4 mm2 | 600 | 540 | 220 | 2.4545 | 3 | 7.66 | 0.051278 | √ |  |  | 13 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
14 | 3x4 mm2 | 600 | 540 | 220 | 2.4545 | 3 | 7.66 | 0.051278 | √ |  |  | 14 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
15 | 3x4 mm2 | 600 | 540 | 220 | 2.4545 | 3 | 7.66 | 0.051278 | √ |  |  | 15 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
16 | 3x4 mm2 | 600 | 540 | 220 |  | 3 | 7.66 | 0 | √ |  |  | 16 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
17 | 3x4 mm2 | 400 | 360 | 220 | 1.6364 | 2 | 7.66 | 0.02279 | √ |  |  | 17 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
18 | 3x4 mm2 | 400 | 360 | 220 | 1.6364 | 2 | 7.66 | 0.02279 | √ |  |  | 18 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
POWER(1)
|  | N | F1 | F2
|  | 1 | POWER S |  | 1500
|  | 2 |  |  | 1500
|  | 3 |  |  | 1500
|  | 4 |  |  | 1500
|  | 5 |  |  | 1500
|  | 6 |  |  | 1500
|  | 7 |  |  | 1500
|  | 8 |  |  | 1500
|  | 9 |  |  | 1500
|  | 10 |  |  | 1500
|  | 11 |  | 4 | 800
|  | 12 |  | 5 | 1000
600
600
600
600
[5 empty] | 400 | [8 empty] | 13 |  | 3 | 600
400
[14 empty] | 14 |  | 3 | 600
|  |  | POWER | [10 empty] | 15 |  | 3 | 600
[14 empty] | 16 |  | 3 | 600
[14 empty] | 17 |  | 2 | 400
|  |  | NO OF CIR | F1 | F2 |  |  | TOTAL
|  |  | 1 | 97 | 1 |  |  | 99
|  |  | 2 | 92 | 1 |  |  | 94
|  |  | 3 | 106 | 1 |  |  | 108 |  | F1 | LENGTH(in between + from panel)
|  |  | 4 | 112 | 1 |  |  | 114 |  | F2 | no of SOCKETS
|  |  | 5 | 114 | 1 |  |  | 116
|  |  | 6 | 121 | 1 |  |  | 123
|  |  | 7 | 87 | 1 |  |  | 89
|  |  | 8 | 92 | 1 |  |  | 94
|  |  | 9 | 147 | 1 |  |  | 149
|  |  | 10 | 153 | 1 |  |  | 155
|  |  | 11 | 156 | 4 |  |  | 4
|  |  | 12 | 35 | 4 |  |  | 5
|  |  | 13 | 92 | 4 |  |  | 3
|  |  | 14 | 93 | 4 |  |  | 3
|  |  | 15 | 76 | 4 |  |  | 3
|  |  | 16 | 78 | 4 |  |  | 3
|  |  | 17 | 100 | 4 |  |  | 2
|  |  | 18 | 48 | 4 |  |  | 2
total length from panel equal 250 m & average lenghth equal 20 m total length (in between and from panel) equal 630m & average 49 m
in case of single phase
%𝑉.𝐷=((2∗𝑅∗𝐼∗𝐿)∗100)/((𝑉)∗1000)→ ((<2%))
in case of single phase
in case of three phase
%𝑉.𝐷=((√3∗𝑅∗𝐼∗𝐿)∗100)/((𝑉)∗1000)→((<3%))
in case of three phase
A(t)=A1+A2+A3+... where : A1 -1 cable in pipe A2- 2 cable in pipe A3-3cable in pipe
A(T)= total C.S.A of cableinside pipe D=outside dimmeter of cable from catalogue
max occupancy ratio :1C=53%fill , 2C=31%fill 3C+=40%fill
𝐹.𝑅=(𝐶.𝑆.𝐴 𝑜𝑓 𝑐𝑎𝑏𝑙𝑒𝑠)/(𝐶.𝑆.𝐴 𝑜𝑓 𝑝𝑖𝑝𝑒)∗100=𝐴(𝑡)/(𝐶.𝑆.𝐴 𝑜𝑓 𝑝𝑖𝑝𝑒)((<53%→1𝐶<31%→2𝐶<40%→+3𝐶))
A(t)=A1+A2+A3+... 𝐴=(𝜋/4) 𝐷^(2 )=0.79𝐷^(2 ) where : A1 -1 cable in pipe A2- 2 cable in pipe A3-3cable in pipe
A(T)= total C.S.A of cableinside pipe D=outside dimmeter of cable from catalogue
max occupancy ratio :1C=53%fill , 2C=31%fill 3C+=40%fill

## CLB-B
Voltage drop calculation for DWG NO |  |  |  |  | CR05-05-EL-AD-10G | [6 empty] | filling calculation for DWG NO |  |  | M
voltage drop calculation | [11 empty] | filling ratio calculation
circuit |  | load |  |  |  | cable |  | results |  |  |  | circuit | c.s.a of cables |  |  |  |  | c.s.a of pipes | results
circuit no | conductor | load-VA | D.LOAD-VA | voltage-V | current-A | length-mt | R-ohm/km | %V.D | acceptance |  |  | no of cabe in pipe | OD-mm | A1-mm² | A2-mm² | A3-mm² | A(t)-mm² | conduit -mm² by inner diammeter | %fill ratio | acceptance
CLB-B | [11 empty] | LPPG2
1 | 3x3 mm2 | 412.25 | 371.025 | 220 | 1.6865 | 200.7 | 7.66 | 2.357 | √ |  |  | 1 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
2 | 3x3 mm3 | 61.25 | 55.125 | 221 | 0.24943 | 119.3 | 7.66 | 0.20628 | √ |  |  | 2 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
3 | 3x3 mm4 | 239.75 | 215.775 | 222 | 0.97196 | 147.5 | 7.66 | 0.98934 | √ |  |  | 3 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
4 | 3x3 mm5 | 61.875 | 55.6875 | 223 | 0.24972 | 142.9 | 7.66 | 0.24515 | √ |  |  | 4 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
5 | 3x3 mm6 | 49.5 | 44.55 | 224 | 0.19888 | 148.7 | 7.66 | 0.20227 | √ |  |  | 5 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
6 | 3x3 mm7 | 49.5 | 44.55 | 225 | 0.198 | 153.7 | 7.66 | 0.20721 | √ |  |  | 6 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
7 | 3x3 mm8 | 230 | 207 | 226 | 0.91593 | 70.5 | 7.66 | 0.43772 | √ |  |  | 7 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
8 | 3x3 mm9 | 230 | 207 | 227 | 0.91189 | 75.5 | 7.66 | 0.46465 | √ |  |  | 8 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
9 | 3x3 mm10 | 143.75 | 129.375 | 228 | 0.56743 | 66.9 | 7.66 | 0.25507 | √ |  |  | 9 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
10 | 3x3 mm11 | 74.25 | 66.825 | 229 | 0.29181 | 144.1 | 7.66 | 0.28131 | √ |  |  | 10 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
11 | 3x3 mm12 | 49.5 | 44.55 | 230 | 0.1937 | 115.7 | 7.66 | 0.14927 | √ |  |  | 11 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
12 | 3x3 mm13 | 258.75 | 232.875 | 231 | 1.0081 | 134.7 | 7.66 | 0.90059 | √ |  |  | 12 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
13 | 3x3 mm14 | 230 | 207 | 232 | 0.89224 | 131.5 | 7.66 | 0.77478 | √ |  |  | 13 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
14 | 3x3 mm15 | 244.5 | 220.05 | 233 | 0.94442 | 130.5 | 7.66 | 0.81036 | √ |  |  | 14 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
15 | 3x3 mm16 | 0 | 0 | 234 | 0 | 86.9 | 7.66 | 0 | √ |  |  | 15 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
16 | 3x3 mm17 | 28.75 | 25.875 | 235 | 0.11011 | 96.1 | 7.66 | 0.068981 | √ |  |  | 16 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
17 | 3x3 mm18 | 136.125 | 122.5125 | 236 | 0.51912 | 122.1 | 7.66 | 0.41146 | √ |  |  | 17 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
18 | 3x3 mm19 | 345 | 310.5 | 237 | 1.3101 | 133.3 | 7.66 | 1.1289 | √ |  |  | 18 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
19 | 3x3 mm20 | 91.875 | 82.6875 | 238 | 0.34743 | 57.5 | 7.66 | 0.12859 | √ |  |  | 19 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
20 | 3x3 mm21 | 311.375 | 280.2375 | 239 | 1.1725 | 96.5 | 7.66 | 0.7253 | √ |  |  | 20 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
21 | 3x3 mm22 | 311.375 | 280.2375 | 240 | 1.1677 | 103.5 | 7.66 | 0.77144 | √ |  |  | 21 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
22 | 3x3 mm23 | 115 | 103.5 | 241 | 0.42946 | 64.7 | 7.66 | 0.17663 | √ |  |  | 22 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
23 | 3x3 mm24 | 115 | 103.5 | 242 | 0.42769 | 70.7 | 7.66 | 0.19142 | √ |  |  | 23 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
24 | 3x3 mm25 | 115 | 103.5 | 243 | 0.42593 | 74.7 | 7.66 | 0.20059 | √ |  |  | 24 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
25 | 3x3 mm26 | 115 | 103.5 | 244 | 0.42418 | 79.7 | 7.66 | 0.21226 | √ |  |  | 25 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
26 | 3x3 mm27 | 115 | 103.5 | 245 | 0.42245 | 68.7 | 7.66 | 0.18148 | √ |  |  | 26 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
27 | 3x3 mm28 | 115 | 103.5 | 246 | 0.42073 | 72.7 | 7.66 | 0.19049 | √ |  |  | 27 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
28 | 3x3 mm29 | 111.375 | 100.2375 | 247 | 0.40582 | 69.7 | 7.66 | 0.17544 | √ |  |  | 28 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
29 | 3x3 mm30 | 61.875 | 55.6875 | 248 | 0.22455 | 60.9 | 7.66 | 0.084475 | √ |  |  | 29 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
30 | 3x3 mm31 | 172.5 | 155.25 | 249 | 0.62349 | 58.1 | 7.66 | 0.22288 | √ |  |  | 30 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
31 | 3x3 mm32 | 149.5 | 134.55 | 250 | 0.5382 | 52.6 | 7.66 | 0.17348 | √ |  |  | 31 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
32 | 3x3 mm33 | 218 | 196.2 | 251 | 0.78167 | 92.8 | 7.66 | 0.44275 | √ |  |  | 32 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
33 | 3x3 mm34 | 172.5 | 155.25 | 252 | 0.61607 | 54.1 | 7.66 | 0.20262 | √ |  |  | 33 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
34 | 3x3 mm35 | 218 | 196.2 | 253 | 0.77549 | 218.1 | 7.66 | 1.0242 | √ |  |  | 34 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
35 | 3x3 mm36 | 82.25 | 74.025 | 254 | 0.29144 | 45.7 | 7.66 | 0.080332 | √ |  |  | 35 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
36 | 3x3 mm37 | 197.25 | 177.525 | 255 | 0.69618 | 71.5 | 7.66 | 0.29905 | √ |  |  | 36 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
37 | 3x3 mm38 | 245 | 220.5 | 256 | 0.86133 | 54.5 | 7.66 | 0.28092 | √ |  |  | 37 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
38 | 3x3 mm39 | 156.125 | 140.5125 | 257 | 0.54674 | 59.1 | 7.66 | 0.19262 | √ |  |  | 38 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
39 | 3x3 mm40 | 201.25 | 181.125 | 258 | 0.70203 | 69.8 | 7.66 | 0.29097 | √ |  |  | 39 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
40 | 3x3 mm41 | 99 | 89.1 | 259 | 0.34402 | 90.5 | 7.66 | 0.18416 | √ |  |  | 40 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
41 | 3x3 mm42 | 57.5 | 51.75 | 260 | 0.19904 | 36.3 | 7.66 | 0.042572 | √ |  |  | 41 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
42 | 3x3 mm43 | 299 | 269.1 | 261 | 1.031 | 87.3 | 7.66 | 0.52833 | √ |  |  | 42 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
43 | 3x3 mm44 | 299 | 269.1 | 262 | 1.0271 | 194.3 | 7.66 | 1.1669 | √ |  |  | 43 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
44 | 3x3 mm45 | 74.25 | 66.825 | 263 | 0.25409 | 184.1 | 7.66 | 0.27248 | √ |  |  | 44 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
45 | 3x3 mm46 | 86.625 | 77.9625 | 264 | 0.29531 | 99.3 | 7.66 | 0.17017 | √ |  |  | 45 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
46 | 3x3 mm47 | 49.5 | 44.55 | 265 | 0.16811 | 158.7 | 7.66 | 0.15424 | √ |  |  | 46 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
47 | 3x3 mm48 | 650 | 585 | 266 | 2.1992 | 259.5 | 7.66 | 3.2869 | √ |  |  | 47 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
48 | 3x3 mm49 | 0 | 0 | 267 | 0 | 1.9 | 7.66 | 0 | √ |  |  | 48 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
49 | 3x3 mm50 | 69.875 | 62.8875 | 268 | 0.23465 | 174.5 | 7.66 | 0.23407 | √ |  |  | 49 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
50 | 3x3 mm51 | 149.5 | 134.55 | 269 | 0.50019 | 187.1 | 7.66 | 0.53298 | √ |  |  | 50 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
51 | 3x3 mm52 | 69.875 | 62.8875 | 270 | 0.23292 | 184.5 | 7.66 | 0.24383 | √ |  |  | 51 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
52 | 3x3 mm53 | 176.875 | 159.1875 | 271 | 0.58741 | 219.7 | 7.66 | 0.72956 | √ |  |  | 52 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
53 | 3x3 mm54 | 426.375 | 383.7375 | 272 | 1.4108 | 257.3 | 7.66 | 2.0445 | √ |  |  | 53 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
54 | 3x3 mm55 | 311.375 | 280.2375 | 273 | 1.0265 | 245.5 | 7.66 | 1.4142 | √ |  |  | 54 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
55 | 3x3 mm56 | 230 | 207 | 274 | 0.75547 | 225.5 | 7.66 | 0.95252 | √ |  |  | 55 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
56 | 3x3 mm57 | 172.5 | 155.25 | 275 | 0.56455 | 79.1 | 7.66 | 0.24877 | √ |  |  | 56 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
57 | 3x3 mm58 | 149.5 | 134.55 | 276 | 0.4875 | 67.1 | 7.66 | 0.18157 | √ |  |  | 57 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
58 | 3x3 mm59 | 82.25 | 74.025 | 277 | 0.26724 | 58.7 | 7.66 | 0.086759 | √ |  |  | 58 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
[19 empty] | 9.9 | 23 | 40 | 8 | 24.5 | 39
|  |  | LIGHTING | [14 empty] | N | f1 | f2 | sh | exit | f3 | f4 | TOTAL
[18 empty] | 1 | 2 | 10 | 2 |  |  |  | 329.8
[18 empty] | 2 |  |  |  |  | 2 |  | 49
|  |  | NO OF CIR | F1 | F2 |  |  | TOTAL | [9 empty] | 3 | 2 | 4 | 2 |  |  |  | 191.8
|  |  | 1 | 140 | 14 |  |  | 200.7 | [8 empty] | condactor | 4 | 5 | [5 empty] | 49.5
|  |  | 2 | 109 | 2 |  |  | 119.3 | [9 empty] | 5 | 4 | [5 empty] | 39.6
|  |  | 3 | 112 | 8 |  |  | 147.5 | [9 empty] | 6 | 4 | [5 empty] | 39.6
|  |  | 4 | 120 | 5 |  |  | 142.9 | [9 empty] | 7 |  | 8 |  |  |  |  | 184
|  |  | 5 | 130 | 4 |  |  | 148.7 |  | F1 | LENGTH(in between + from panel) | [6 empty] | 8 |  | 8 |  |  |  |  | 184
|  |  | 6 | 135 | 4 |  |  | 153.7 |  | F2 | no of ligting | [6 empty] | 9 |  | 5 |  |  |  |  | 115
|  |  | 7 | 35 | 8 |  |  | 70.5 |  | 1.9 | H OF FLOOR-2 | [6 empty] | 10 | 6 | [5 empty] | 59.4
|  |  | 8 | 40 | 8 |  |  | 75.5 | [9 empty] | 11 | 4 | [5 empty] | 39.6
|  |  | 9 | 44 | 5 |  |  | 66.9 | [9 empty] | 12 |  | 9 |  |  |  |  | 207
|  |  | 10 | 117 | 6 |  |  | 144.1 | [9 empty] | 13 |  | 8 |  |  |  |  | 184
|  |  | 11 | 97 | 4 |  |  | 115.7 | [9 empty] | 14 | 4 |  |  |  |  | 4 | 195.6
|  |  | 12 | 95 | 9 |  |  | 134.7
|  |  | 13 | 96 | 8 |  |  | 131.5
|  |  | 14 | 95 | 8 |  |  | 130.5
|  |  | 15 | 85 | 0 |  |  | 86.9
|  |  | 16 | 90 | 1 |  |  | 96.1
|  |  | 17 | 74 | 11 |  |  | 122.1
|  |  | 18 | 81 | 12 |  |  | 133.3
|  |  | 19 | 43 | 3 |  |  | 57.5
|  |  | 20 | 40 | 13 |  |  | 96.5
|  |  | 21 | 47 | 13 |  |  | 103.5
|  |  | 22 | 46 | 4 |  |  | 64.7
|  |  | 23 | 52 | 4 |  |  | 70.7
|  |  | 24 | 56 | 4 |  |  | 74.7
|  |  | 25 | 61 | 4 |  |  | 79.7
|  |  | 26 | 50 | 4 |  |  | 68.7
|  |  | 27 | 54 | 4 |  |  | 72.7
|  |  | 28 | 30 | 9 |  |  | 69.7
|  |  | 29 | 38 | 5 |  |  | 60.9
|  |  | 30 | 31 | 6 |  |  | 58.1
|  |  | 31 | 25.5 | 6 |  |  | 52.6
|  |  | 32 | 44.7 | 11 |  |  | 92.8
|  |  | 33 | 27 | 6 |  |  | 54.1
|  |  | 34 | 170 | 11 |  |  | 218.1
|  |  | 35 | 27 | 4 |  |  | 45.7
|  |  | 36 | 36 | 8 |  |  | 71.5
|  |  | 37 | 19 | 8 |  |  | 54.5
|  |  | 38 | 32 | 6 |  |  | 59.1
|  |  | 39 | 38.5 | 7 |  |  | 69.8
|  |  | 40 | 55 | 8 |  |  | 90.5
|  |  | 41 | 26 | 2 |  |  | 36.3
|  |  | 42 | 35 | 12 |  |  | 87.3
|  |  | 43 | 142 | 12 |  |  | 194.3
|  |  | 44 | 157 | 6 |  |  | 184.1
|  |  | 45 | 68 | 7 |  |  | 99.3
|  |  | 46 | 140 | 4 |  |  | 158.7
|  |  | 47 | 203 | 13 |  |  | 259.5
|  |  | 48 | 0 | 0 |  |  | 1.9
|  |  | 49 | 160 | 3 |  |  | 174.5
|  |  | 50 | 160 | 6 |  |  | 187.1
|  |  | 51 | 170 | 3 |  |  | 184.5
|  |  | 52 | 180 | 9 |  |  | 219.7
|  |  | 53 | 184 | 17 |  |  | 257.3
|  |  | 54 | 189 | 13 |  |  | 245.5
|  |  | 55 | 190 | 8 |  |  | 225.5
|  |  | 56 | 52 | 6 |  |  | 79.1
|  |  | 57 | 40 | 6 |  |  | 67.1
|  |  | 58 | 40 | 4 |  |  | 58.7
[18 empty] | 16 |  | 1 |  |  |  |  | 23
[18 empty] | 17 | 11 | [5 empty] | 108.9
[17 empty] | condactor | 18 |  | 12 |  |  |  |  | 276
[18 empty] | 19 |  |  |  |  | 3 |  | 73.5
[17 empty] | ELCB | 20 | 9 |  | 4 |  |  |  | 249.1
[17 empty] | ELCB | 21 | 9 |  | 4 |  |  |  | 249.1
[18 empty] | 22 |  | 4 |  |  |  |  | 92
[18 empty] | 23 |  | 4 |  |  |  |  | 92
[18 empty] | 24 |  | 4 |  |  |  |  | 92
[18 empty] | 25 |  | 4 |  |  |  |  | 92
[18 empty] | 26 |  | 4 |  |  |  |  | 92
[18 empty] | 27 |  | 4 |  |  |  |  | 92
[17 empty] | condactor | 28 | 9 | [5 empty] | 89.1
[18 empty] | 29 | 5 | [5 empty] | 49.5
[18 empty] | 30 |  | 6 |  |  |  |  | 138
[18 empty] | 31 | 4 |  | 2 |  |  |  | 119.6
[18 empty] | 32 | 6 | 5 |  |  |  |  | 174.4
[18 empty] | 33 |  | 6 |  |  |  |  | 138
[18 empty] | 34 | 6 | 5 |  |  |  |  | 174.4
[18 empty] | 35 | 2 | 2 |  |  |  |  | 65.8
[18 empty] | 36 | 2 | 6 |  |  |  |  | 157.8
[18 empty] | 37 |  |  |  |  | 8 |  | 196
[18 empty] | 38 | 1 | 5 |  |  |  |  | 124.9
[18 empty] | 39 |  | 7 |  |  |  |  | 161
[17 empty] | condactor | 40 | 8 | [5 empty] | 79.2
[18 empty] | 41 |  | 2 |  |  |  |  | 46
[18 empty] | 42 | 8 |  | 4 |  |  |  | 239.2
[18 empty] | 43 | 8 |  | 4 |  |  |  | 239.2
[17 empty] | condactor | 44 | 6 | [5 empty] | 59.4
[17 empty] | condactor | 45 | 7 | [5 empty] | 69.3
[18 empty] | 46 | 4 | [5 empty] | 39.6
[18 empty] | 47 |  |  | 13 |  |  |  | 520
[18 empty] | 48 | [6 empty] | 0
[18 empty] | 49 | 1 | 2 |  |  |  |  | 55.9
[18 empty] | 50 | 4 |  | 2 |  |  |  | 119.6
[18 empty] | 51 | 1 | 2 |  |  |  |  | 55.9
[17 empty] | condactor | 52 | 5 | 4 |  |  |  |  | 141.5
[18 empty] | 53 | 9 | 4 | 4 |  |  |  | 341.1
[18 empty] | 54 | 9 |  | 4 |  |  |  | 249.1
[18 empty] | 55 |  | 8 |  |  |  |  | 184
[18 empty] | 56 |  | 6 |  |  |  |  | 138
[18 empty] | 57 | 4 |  | 2 |  |  |  | 119.6
[18 empty] | 58 | 2 | 2 |  |  |  |  | 65.8
|  |  |  | 9.9 | 23 | 40 | 8 | 24.5 | 39
|  |  | N | f1 | f2 | sh | exit | f3 | f4 |  | TOTAL | NUM | LEN
|  |  | 1 | 2 | 10 | 2 |  |  |  |  | 329.8 | 14 | 140
|  |  | 2 |  |  |  |  | 2 |  |  | 49 | 2 | 109
|  |  | 3 | 2 | 4 | 2 |  |  |  |  | 191.8 | 8 | 112
|  | condactor | 4 | 5 | [6 empty] | 49.5 | 5 | 120
|  |  | 5 | 4 | [6 empty] | 39.6 | 4 | 130
|  |  | 6 | 4 | [6 empty] | 39.6 | 4 | 135
|  |  | 7 |  | 8 | [5 empty] | 184 | 8 | 35
|  |  | 8 |  | 8 | [5 empty] | 184 | 8 | 40
|  |  | 9 |  | 5 | [5 empty] | 115 | 5 | 44
|  |  | 10 | 6 | [6 empty] | 59.4 | 6 | 117
|  |  | 11 | 4 | [6 empty] | 39.6 | 4 | 97
|  |  | 12 |  | 9 | [5 empty] | 207 | 9 | 95
|  |  | 13 |  | 8 | [5 empty] | 184 | 8 | 96
|  |  | 14 | 4 |  |  |  |  | 4 |  | 195.6 | 8 | 95
|  |  | 15 | [7 empty] | 0 | 0 | 85
|  |  | 16 |  | 1 | [5 empty] | 23 | 1 | 90
|  |  | 17 | 11 | [6 empty] | 108.9 | 11 | 74
|  | condactor | 18 |  | 12 | [5 empty] | 276 | 12 | 81
|  |  | 19 |  |  |  |  | 3 |  |  | 73.5 | 3 | 43
|  | ELCB | 20 | 9 |  | 4 |  |  |  |  | 249.1 | 13 | 40
|  | ELCB | 21 | 9 |  | 4 |  |  |  |  | 249.1 | 13 | 47
|  |  | 22 |  | 4 | [5 empty] | 92 | 4 | 46
|  |  | 23 |  | 4 | [5 empty] | 92 | 4 | 52
|  |  | 24 |  | 4 | [5 empty] | 92 | 4 | 56
|  |  | 25 |  | 4 | [5 empty] | 92 | 4 | 61
|  |  | 26 |  | 4 | [5 empty] | 92 | 4 | 50
|  |  | 27 |  | 4 | [5 empty] | 92 | 4 | 54
|  | condactor | 28 | 9 | [6 empty] | 89.1 | 9 | 30
|  |  | 29 | 5 | [6 empty] | 49.5 | 5 | 38
|  |  | 30 |  | 6 | [5 empty] | 138 | 6 | 31
|  |  | 31 | 4 |  | 2 |  |  |  |  | 119.6 | 6 | 25.5
|  |  | 32 | 6 | 5 | [5 empty] | 174.4 | 11 | 44.7
|  |  | 33 |  | 6 | [5 empty] | 138 | 6 | 27
|  |  | 34 | 6 | 5 | [5 empty] | 174.4 | 11 | 170
|  |  | 35 | 2 | 2 | [5 empty] | 65.8 | 4 | 27
|  |  | 36 | 2 | 6 | [5 empty] | 157.8 | 8 | 36
|  |  | 37 |  |  |  |  | 8 |  |  | 196 | 8 | 19
|  |  | 38 | 1 | 5 | [5 empty] | 124.9 | 6 | 32
|  |  | 39 |  | 7 | [5 empty] | 161 | 7 | 38.5
|  | condactor | 40 | 8 | [6 empty] | 79.2 | 8 | 55
|  |  | 41 |  | 2 | [5 empty] | 46 | 2 | 26
|  |  | 42 | 8 |  | 4 |  |  |  |  | 239.2 | 12 | 35
|  |  | 43 | 8 |  | 4 |  |  |  |  | 239.2 | 12 | 142
|  | condactor | 44 | 6 | [6 empty] | 59.4 | 6 | 157
|  | condactor | 45 | 7 | [6 empty] | 69.3 | 7 | 68
|  |  | 46 | 4 | [6 empty] | 39.6 | 4 | 140
|  |  | 47 |  |  | 13 |  |  |  |  | 520 | 13 | 203
|  |  | 48 | [7 empty] | 0 | 0 | 0
|  |  | 49 | 1 | 2 | [5 empty] | 55.9 | 3 | 160
|  |  | 50 | 4 |  | 2 |  |  |  |  | 119.6 | 6 | 160
|  |  | 51 | 1 | 2 | [5 empty] | 55.9 | 3 | 170
|  | condactor | 52 | 5 | 4 | [5 empty] | 141.5 | 9 | 180
|  |  | 53 | 9 | 4 | 4 |  |  |  |  | 341.1 | 17 | 184
|  |  | 54 | 9 |  | 4 |  |  |  |  | 249.1 | 13 | 189
|  |  | 55 |  | 8 | [5 empty] | 184 | 8 | 190
|  |  | 56 |  | 6 | [5 empty] | 138 | 6 | 52
|  |  | 57 | 4 |  | 2 |  |  |  |  | 119.6 | 6 | 40
|  |  | 58 | 2 | 2 | [5 empty] | 65.8 | 4 | 40
in case of single phase
%𝑉.𝐷=((2∗𝑅∗𝐼∗𝐿)∗100)/((𝑉)∗1000)→ ((<2%))
in case of single phase
in case of three phase
%𝑉.𝐷=((√3∗𝑅∗𝐼∗𝐿)∗100)/((𝑉)∗1000)→((<3%))
in case of three phase
A(t)=A1+A2+A3+... where : A1 -1 cable in pipe A2- 2 cable in pipe A3-3cable in pipe
A(T)= total C.S.A of cableinside pipe D=outside dimmeter of cable from catalogue
max occupancy ratio :1C=53%fill , 2C=31%fill 3C+=40%fill
𝐹.𝑅=(𝐶.𝑆.𝐴 𝑜𝑓 𝑐𝑎𝑏𝑙𝑒𝑠)/(𝐶.𝑆.𝐴 𝑜𝑓 𝑝𝑖𝑝𝑒)∗100=𝐴(𝑡)/(𝐶.𝑆.𝐴 𝑜𝑓 𝑝𝑖𝑝𝑒)((<53%→1𝐶<31%→2𝐶<40%→+3𝐶))
A(t)=A1+A2+A3+... 𝐴=(𝜋/4) 𝐷^(2 )=0.79𝐷^(2 ) where : A1 -1 cable in pipe A2- 2 cable in pipe A3-3cable in pipe
A(T)= total C.S.A of cableinside pipe D=outside dimmeter of cable from catalogue
max occupancy ratio :1C=53%fill , 2C=31%fill 3C+=40%fill

## NLP-B
Voltage drop calculation for DWG NO |  |  |  |  | CR05-05-EL-AD-10G | [6 empty] | filling calculation for DWG NO |  |  | M
voltage drop calculation | [11 empty] | filling ratio calculation
circuit |  | load |  |  |  | cable |  | results |  |  |  | circuit | c.s.a of cables |  |  |  |  | c.s.a of pipes | results
circuit no | conductor | load-VA | D.LOAD-VA | voltage-V | current-A | length-mt | R-ohm/km | %V.D | acceptance |  |  | no of cabe in pipe | OD-mm | A1-mm² | A2-mm² | A3-mm² | A(t)-mm² | conduit -mm² by inner diammeter | %fill ratio | acceptance
NLP-B | [11 empty] | 1
1 | 3x3 mm2 | 245 | 220.5 | 220 | 1.0023 | 147.8 | 7.66 | 1.0316 | √ |  |  | 1 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
2 | 3x3 mm2 | 452 | 406.8 | 221 | 1.8407 | 204.5 | 7.66 | 2.6094 | √ |  |  | 2 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
3 | 3x3 mm2 | 230 | 207 | 222 | 0.93243 | 163.5 | 7.66 | 1.0521 | √ |  |  | 3 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
4 | 3x3 mm2 | 172.5 | 155.25 | 223 | 0.69619 | 126.1 | 7.66 | 0.60311 | √ |  |  | 4 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
5 | 3x3 mm2 | 49.5 | 44.55 | 224 | 0.19888 | 119.7 | 7.66 | 0.16282 | √ |  |  | 5 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
6 | 3x3 mm2 | 243.75 | 219.375 | 225 | 0.975 | 96.9 | 7.66 | 0.64329 | √ |  |  | 6 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
7 | 3x3 mm2 | 61.875 | 55.6875 | 226 | 0.2464 | 112.9 | 7.66 | 0.18858 | √ |  |  | 7 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
8 | 3x3 mm2 | 0 | 0 | 227 | 0 | 1.9 | 7.66 | 0 | √ |  |  | 8 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
9 | 3x3 mm2 | 99 | 89.1 | 228 | 0.39079 | 122.5 | 7.66 | 0.32166 | √ |  |  | 9 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
10 | 3x3 mm2 | 230 | 207 | 229 | 0.90393 | 125.5 | 7.66 | 0.75893 | √ |  |  | 10 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
11 | 3x3 mm2 | 345 | 310.5 | 230 | 1.35 | 133.3 | 7.66 | 1.1987 | √ |  |  | 11 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
12 | 3x3 mm2 | 99 | 89.1 | 231 | 0.38571 | 152.5 | 7.66 | 0.39011 | √ |  |  | 12 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
13 | 3x3 mm2 | 37.125 | 33.4125 | 232 | 0.14402 | 106.5 | 7.66 | 0.10128 | √ |  |  | 13 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
14 | 3x3 mm2 | 287.5 | 258.75 | 233 | 1.1105 | 129.9 | 7.66 | 0.9485 | √ |  |  | 14 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
15 | 3x3 mm2 | 111.375 | 100.2375 | 234 | 0.42837 | 155.7 | 7.66 | 0.43666 | √ |  |  | 15 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
16 | 3x3 mm2 | 123.75 | 111.375 | 235 | 0.47394 | 178.9 | 7.66 | 0.55274 | √ |  |  | 16 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
17 | 3x3 mm2 | 136.125 | 122.5125 | 236 | 0.51912 | 201.1 | 7.66 | 0.67768 | √ |  |  | 17 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
18 | 3x3 mm2 | 99 | 89.1 | 237 | 0.37595 | 185.5 | 7.66 | 0.4508 | √ |  |  | 18 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
19 | 3x3 mm2 | 258.75 | 232.875 | 238 | 0.97847 | 197.7 | 7.66 | 1.2452 | √ |  |  | 19 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
20 | 3x3 mm2 | 337 | 303.3 | 239 | 1.269 | 195.7 | 7.66 | 1.5919 | √ |  |  | 20 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
21 | 3x3 mm2 | 74.25 | 66.825 | 240 | 0.27844 | 60.1 | 7.66 | 0.10682 | √ |  |  | 21 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
22 | 3x3 mm2 | 258.75 | 232.875 | 241 | 0.96629 | 196.7 | 7.66 | 1.2082 | √ |  |  | 22 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
23 | 3x3 mm2 | 164.5 | 148.05 | 242 | 0.61178 | 187.5 | 7.66 | 0.72617 | √ |  |  | 23 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
24 | 3x3 mm2 | 230 | 207 | 243 | 0.85185 | 215.5 | 7.66 | 1.1573 | √ |  |  | 24 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
25 | 3x3 mm2 | 86.25 | 77.625 | 244 | 0.31814 | 58.5 | 7.66 | 0.11685 | √ |  |  | 25 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
26 | 3x3 mm2 | 86.625 | 77.9625 | 245 | 0.31821 | 84.8 | 7.66 | 0.16874 | √ |  |  | 26 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
27 | 3x3 mm2 | 99 | 89.1 | 246 | 0.3622 | 57.9 | 7.66 | 0.1306 | √ |  |  | 27 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
28 | 3x3 mm2 | 287.5 | 258.75 | 247 | 1.0476 | 140.9 | 7.66 | 0.9155 | √ |  |  | 28 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
29 | 3x3 mm2 | 74.25 | 66.825 | 248 | 0.26946 | 128.1 | 7.66 | 0.21323 | √ |  |  | 29 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
30 | 3x3 mm2 | 287.5 | 258.75 | 249 | 1.0392 | 130.9 | 7.66 | 0.83691 | √ |  |  | 30 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
31 | 3x3 mm2 | 287.5 | 258.75 | 250 | 1.035 | 121.9 | 7.66 | 0.77315 | √ |  |  | 31 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
32 | 3x3 mm2 | 98.625 | 88.7625 | 251 | 0.35364 | 45.7 | 7.66 | 0.098641 | √ |  |  | 32 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
33 | 3x3 mm2 | 299.875 | 269.8875 | 252 | 1.071 | 106.9 | 7.66 | 0.69601 | √ |  |  | 33 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
34 | 3x3 mm2 | 287.5 | 258.75 | 253 | 1.0227 | 65.9 | 7.66 | 0.40812 | √ |  |  | 34 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
35 | 3x3 mm2 | 74.25 | 66.825 | 254 | 0.26309 | 27.1 | 7.66 | 0.043003 | √ |  |  | 35 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
36 | 3x3 mm2 | 245 | 220.5 | 255 | 0.86471 | 106.78 | 7.66 | 0.55472 | √ |  |  | 36 | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
LIGHTING
|  |  | NO OF CIR | F1 | F2 |  |  | TOTAL
|  |  | 1 | 113 | 8 |  |  | 147.8
|  |  | 2 | 127 | 18 |  |  | 204.5
|  |  | 3 | 128 | 8 |  |  | 163.5
|  |  | 4 | 99 | 6 |  |  | 126.1
|  |  | 5 | 101 | 4 |  |  | 119.7 |  | F1 | LENGTH(in between + from panel)
|  |  | 6 | 74 | 5 |  |  | 96.9 |  | F2 | no of ligting
|  |  | 7 | 90 | 5 |  |  | 112.9 |  | 2 | H OF FLOOR-2
|  |  | 8 | 0 | 0 |  |  | 1.9
|  |  | 9 | 87 | 8 |  |  | 122.5
|  |  | 10 | 90 | 8 |  |  | 125.5
|  |  | 11 | 81 | 12 |  |  | 133.3
|  |  | 12 | 117 | 8 |  |  | 152.5
|  |  | 13 | 92 | 3 |  |  | 106.5
|  |  | 14 | 86 | 10 |  |  | 129.9
|  |  | 15 | 116 | 9 |  |  | 155.7
|  |  | 16 | 135 | 10 |  |  | 178.9
|  |  | 17 | 153 | 11 |  |  | 201.1
|  |  | 18 | 150 | 8 |  |  | 185.5
|  |  | 19 | 158 | 9 |  |  | 197.7
|  |  | 20 | 135 | 14 |  |  | 195.7
|  |  | 21 | 33 | 6 |  |  | 60.1
|  |  | 22 | 157 | 9 |  |  | 196.7
|  |  | 23 | 152 | 8 |  |  | 187.5
|  |  | 24 | 180 | 8 |  |  | 215.5
|  |  | 25 | 44 | 3 |  |  | 58.5
|  |  | 26 | 53.5 | 7 |  |  | 84.8
|  |  | 27 | 22.4 | 8 |  |  | 57.9
|  |  | 28 | 97 | 10 |  |  | 140.9
|  |  | 29 | 101 | 6 |  |  | 128.1
|  |  | 30 | 87 | 10 |  |  | 130.9
|  |  | 31 | 78 | 10 |  |  | 121.9
|  |  | 32 | 27 | 4 |  |  | 45.7
|  |  | 33 | 58.8 | 11 |  |  | 106.9
|  |  | 34 | 22 | 10 |  |  | 65.9
|  |  | 35 | 0 | 6 |  |  | 27.1
|  |  | 36 | 71.28 | 8 |  |  | 106.78
[5 empty] | 9.9 | 23 | 24.5 | 39
|  |  |  | N | F1 | F2 | F3 | F4 |  | TOTAL | N | L
|  |  |  | 1 |  |  | 8 |  |  | 196 | 8 | 113
|  |  |  | 2 | 4 | 14 |  |  |  | 361.6 | 18 | 127
|  |  | contactor | 3 |  | 8 |  |  |  | 184 | 8 | 128
|  |  |  | 4 |  | 6 |  |  |  | 138 | 6 | 99
|  |  |  | 5 | 4 |  |  |  |  | 39.6 | 4 | 101
|  |  |  | 6 |  |  |  | 5 |  | 195 | 5 | 74
|  |  |  | 7 | 5 |  |  |  |  | 49.5 | 5 | 90
|  |  |  | 8 | [5 empty] | 0 | 0 | 0
|  |  | contactor | 9 | 8 |  |  |  |  | 79.2 | 8 | 87
|  |  | contactor | 10 |  | 8 |  |  |  | 184 | 8 | 90
|  |  | contactor | 11 |  | 12 |  |  |  | 276 | 12 | 81
|  |  |  | 12 | 8 |  |  |  |  | 79.2 | 8 | 117
|  |  |  | 13 | 3 |  |  |  |  | 29.7 | 3 | 92
|  |  |  | 14 |  | 10 |  |  |  | 230 | 10 | 86
|  |  |  | 15 | 9 |  |  |  |  | 89.1 | 9 | 116
|  |  |  | 16 | 10 |  |  |  |  | 99 | 10 | 135
|  |  | contactor | 17 | 11 |  |  |  |  | 108.9 | 11 | 153
|  |  | contactor | 18 | 8 |  |  |  |  | 79.2 | 8 | 150
|  |  |  | 19 |  | 9 |  |  |  | 207 | 9 | 158
|  |  | contactor | 20 | 4 | 10 |  |  |  | 269.6 | 14 | 135
|  |  |  | 21 | 6 |  |  |  |  | 59.4 | 6 | 33
|  |  |  | 22 |  | 9 |  |  |  | 207 | 9 | 157
|  |  |  | 23 | 4 | 4 |  |  |  | 131.6 | 8 | 152
|  |  |  | 24 |  | 8 |  |  |  | 184 | 8 | 180
|  |  |  | 25 |  | 3 |  |  |  | 69 | 3 | 44
|  |  |  | 26 | 7 |  |  |  |  | 69.3 | 7 | 53.5
|  |  |  | 27 | 8 |  |  |  |  | 79.2 | 8 | 22.4
|  |  |  | 28 |  | 10 |  |  |  | 230 | 10 | 97
|  |  |  | 29 | 6 |  |  |  |  | 59.4 | 6 | 101
|  |  |  | 30 |  | 10 |  |  |  | 230 | 10 | 87
|  |  |  | 31 |  | 10 |  |  |  | 230 | 10 | 78
|  |  |  | 32 | 1 | 3 |  |  |  | 78.9 | 4 | 27 | [5 empty] | 9.9 | 23 | 24.5 | 39
|  |  |  | 33 | 1 | 10 |  |  |  | 239.9 | 11 | 58.8 |  |  |  |  | N | F1 | F2 | F3 | F4 | TOTAL | عدد الكشافات
|  |  |  | 34 |  | 10 |  |  |  | 230 | 10 | 22 |  |  |  |  | 1 |  |  | 8 |  | 196 | 8
|  |  | contactor | 35 | 6 |  |  |  |  | 59.4 | 6 | 0 |  |  |  |  | 2 | 4 | 14 |  |  | 361.6 | 18
|  |  |  | 36 |  |  | 8 |  |  | 196 | 8 | 71.28 |  |  |  | contactor | 3 |  | 8 |  |  | 184 | 8
[17 empty] | 4 |  | 6 |  |  | 138 | 6
[17 empty] | 5 | 4 |  |  |  | 39.6 | 4
[17 empty] | 6 |  |  |  | 5 | 195 | 5
[17 empty] | 7 | 5 |  |  |  | 49.5 | 5
[17 empty] | 8 |  |  |  |  | 0 | 0
[16 empty] | contactor | 9 | 8 |  |  |  | 79.2 | 8
[16 empty] | contactor | 10 |  | 8 |  |  | 184 | 8
[16 empty] | contactor | 11 |  | 12 |  |  | 276 | 12
[17 empty] | 12 | 8 |  |  |  | 79.2 | 8
[17 empty] | 13 | 3 |  |  |  | 29.7 | 3
[17 empty] | 14 |  | 10 |  |  | 230 | 10
[17 empty] | 15 | 9 |  |  |  | 89.1 | 9
[17 empty] | 16 | 10 |  |  |  | 99 | 10
[16 empty] | contactor | 17 | 11 |  |  |  | 108.9 | 11
[16 empty] | contactor | 18 | 8 |  |  |  | 79.2 | 8
[17 empty] | 19 |  | 9 |  |  | 207 | 9
[16 empty] | contactor | 20 | 4 | 10 |  |  | 269.6 | 14
[17 empty] | 21 | 6 |  |  |  | 59.4 | 6
[17 empty] | 22 |  | 9 |  |  | 207 | 9
[17 empty] | 23 | 4 | 4 |  |  | 131.6 | 8
[17 empty] | 24 |  | 8 |  |  | 184 | 8
[17 empty] | 25 |  | 3 |  |  | 69 | 3
[17 empty] | 26 | 7 |  |  |  | 69.3 | 7
[17 empty] | 27 | 8 |  |  |  | 79.2 | 8
[17 empty] | 28 |  | 10 |  |  | 230 | 10
[17 empty] | 29 | 6 |  |  |  | 59.4 | 6
[17 empty] | 30 |  | 10 |  |  | 230 | 10
[17 empty] | 31 |  | 10 |  |  | 230 | 10
[17 empty] | 32 | 1 | 3 |  |  | 78.9 | 4
[17 empty] | 33 | 1 | 10 |  |  | 239.9 | 11
[17 empty] | 34 |  | 10 |  |  | 230 | 10
[16 empty] | contactor | 35 | 6 |  |  |  | 59.4 | 6
[17 empty] | 36 |  |  | 8 |  | 196 | 8
in case of single phase
%𝑉.𝐷=((2∗𝑅∗𝐼∗𝐿)∗100)/((𝑉)∗1000)→ ((<2%))
in case of single phase
in case of three phase
%𝑉.𝐷=((√3∗𝑅∗𝐼∗𝐿)∗100)/((𝑉)∗1000)→((<3%))
in case of three phase
A(t)=A1+A2+A3+... where : A1 -1 cable in pipe A2- 2 cable in pipe A3-3cable in pipe
A(T)= total C.S.A of cableinside pipe D=outside dimmeter of cable from catalogue
max occupancy ratio :1C=53%fill , 2C=31%fill 3C+=40%fill
𝐹.𝑅=(𝐶.𝑆.𝐴 𝑜𝑓 𝑐𝑎𝑏𝑙𝑒𝑠)/(𝐶.𝑆.𝐴 𝑜𝑓 𝑝𝑖𝑝𝑒)∗100=𝐴(𝑡)/(𝐶.𝑆.𝐴 𝑜𝑓 𝑝𝑖𝑝𝑒)((<53%→1𝐶<31%→2𝐶<40%→+3𝐶))
A(t)=A1+A2+A3+... 𝐴=(𝜋/4) 𝐷^(2 )=0.79𝐷^(2 ) where : A1 -1 cable in pipe A2- 2 cable in pipe A3-3cable in pipe
A(T)= total C.S.A of cableinside pipe D=outside dimmeter of cable from catalogue
max occupancy ratio :1C=53%fill , 2C=31%fill 3C+=40%fill

## NSP2-B (4) (hidden)
Voltage drop calculation for DWG NO |  |  |  |  | CR05-05-EL-AD-10G | [6 empty] | filling calculation for DWG NO |  |  | M
voltage drop calculation | [11 empty] | filling ratio calculation
circuit |  | load |  |  |  | cable |  | results |  |  |  | circuit | c.s.a of cables |  |  |  |  | c.s.a of pipes | results
circuit no | conductor | load-VA | D.LOAD-VA | voltage-V | current-A | length-mt | R-ohm/km | %V.D | acceptance |  |  | no of cabe in pipe | OD-mm | A1-mm² | A2-mm² | A3-mm² | A(t)-mm² | conduit -mm² by inner diammeter | %fill ratio | acceptance
LPPG2 | [11 empty] | LPPG2
1 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 166.7 | 7.66 | 8.9042 | √ |  |  | 1R | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
2 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 125.3 | 7.66 | 6.6928 | √ |  |  | 2R | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
3 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 155.1 | 7.66 | 8.2846 | √ |  |  | 3Y | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
4 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 161.1 | 7.66 | 8.605 | √ |  |  | 4Y | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
5 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 139.1 | 7.66 | 7.4299 | √ |  |  | 5B | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
6 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 120.7 | 7.66 | 6.4471 | √ |  |  | 6B | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
7 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 159.9 | 7.66 | 8.5409 | √ |  |  | 7R | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
8 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 106.7 | 7.66 | 5.6993 | √ |  |  | 8R | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
9 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 95.7 | 7.66 | 5.1117 | √ |  |  | 9Y | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
10 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 85.5 | 7.66 | 4.5669 | √ |  |  | 10Y | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
11 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 71.9 | 7.66 | 3.8405 | √ |  |  | 11B | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
12 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 117.3 | 7.66 | 6.2655 | √ |  |  | 12B | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
13 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 59.4 | 7.66 | 3.1728 | √ |  |  | 13R | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
14 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 51.4 | 7.66 | 2.7455 | √ |  |  | 14R | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
15 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 100.2 | 7.66 | 5.3521 | √ |  |  | 15Y | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
16 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 20.6 | 5.88 | 0.84464 | √ |  |  | 16Y | 12.8 | 129.4336 | 0 | 0 | 129.4336 | 352.81 | 36.6865 | √
17 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 10.6 | 5.88 | 0.43462 | √ |  |  | 17B | 12.8 | 129.4336 | 0 | 0 | 129.4336 | 352.81 | 36.6865 | √
18 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 80.4 | 7.66 | 4.2945 | √ |  |  | 18B | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
19 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 65.4 | 5.88 | 2.6815 | √ |  |  | 19R | 12.8 | 129.4336 | 0 | 0 | 129.4336 | 352.81 | 36.6865 | √
20 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 87.6 | 5.88 | 3.5918 | √ |  |  | 20R | 12.8 | 129.4336 | 0 | 0 | 129.4336 | 352.81 | 36.6865 | √
21 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 70.4 | 7.66 | 3.7604 | √ |  |  | 21Y | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
22 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 76.2 | 7.66 | 4.0702 | √ |  |  | 22Y | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
23 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 90.4 | 7.66 | 4.8286 | √ |  |  | 23B | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
24 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 106 | 3.93 | 2.9049 | √ |  |  | 24B | 14.2 | 159.2956 | 0 | 0 | 159.2956 | 572.265 | 27.836 | √
25 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 78.2 | 7.66 | 4.177 | √ |  |  | 25R | 11.6 | 106.3024 | 0 | 0 | 106.3024 | 352.81 | 30.1302 | √
26 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 63.9 | 5.88 | 2.62 | √ |  |  | 26R | 12.8 | 129.4336 | 0 | 0 | 129.4336 | 352.81 | 36.6865 | √
27 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 48.9 | 5.88 | 2.005 | √ |  |  | 27Y | 12.8 | 129.4336 | 0 | 0 | 129.4336 | 352.81 | 36.6865 | √
28 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 49.9 | 5.88 | 2.046 | √ |  |  | 28Y | 12.8 | 129.4336 | 0 | 0 | 129.4336 | 352.81 | 36.6865 | √
29 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 43.9 | 5.88 | 1.8 | √ |  |  | 29B | 12.8 | 129.4336 | 0 | 0 | 129.4336 | 352.81 | 36.6865 | √
30 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 42.9 | 5.88 | 1.759 | √ |  |  | 30B | 12.8 | 129.4336 | 0 | 0 | 129.4336 | 352.81 | 36.6865 | √
31 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 32.9 | 5.88 | 1.349 | √ |  |  | 31R | 12.8 | 129.4336 | 0 | 0 | 129.4336 | 352.81 | 36.6865 | √
32 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 24.9 | 5.88 | 1.021 | √ |  |  | 32R | 12.8 | 129.4336 | 0 | 0 | 129.4336 | 352.81 | 36.6865 | √
33 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 35.9 | 5.88 | 1.472 | √ |  |  | 33Y | 12.8 | 129.4336 | 0 | 0 | 129.4336 | 352.81 | 36.6865 | √
34 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 22.9 | 5.88 | 0.93895 | √ |  |  | 34Y | 12.8 | 129.4336 | 0 | 0 | 129.4336 | 352.81 | 36.6865 | √
35 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705 | 30.9 | 5.88 | 1.267 | √ |  |  | 35B | 12.8 | 129.4336 | 0 | 0 | 129.4336 | 352.81 | 36.6865 | √
38 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
39 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
40 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
41 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
42 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
43 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
44 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
45 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
46 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
47 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
48 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
49 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
50 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
51 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
52 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
53 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
54 | 3x4 mm2 | 1875 | 1687.5 | 220 | 7.6705
POWER(1)
[16 empty] | N | F1 | F2 | TOTAL(KW) | عدد الكشافات
|  |  | LIGHTING | [12 empty] | 1 | 4 | 6 | 2000 | 10
[16 empty] | 2 | 6 | 2 | 1600 | 8
[16 empty] | 3 | 2 | 4 | 1200 | 6
|  |  | NO OF CIR | F1 | F2 |  |  | TOTAL | [7 empty] | 4 | 6 | 2 | 1600 | 8
|  |  | 1 | 85 | 19 |  |  | 166.7 | [7 empty] | 5 |  |  | 0 | 0
|  |  | 2 | 73 | 12 |  |  | 125.3 | [7 empty] | 6 | 5 |  | 1000 | 5
|  |  | 3 | 86 | 16 |  |  | 155.1 | [7 empty] | 7 | 4 |  | 800 | 4
|  |  | 4 | 92 | 16 |  |  | 161.1 | [7 empty] | 8 | 5 |  | 1000 | 5
|  |  | 5 | 70 | 16 |  |  | 139.1 |  | F1 | LENGTH(in between + from panel) |  |  |  |  | 9 |  | 6 | 1200 | 6
|  |  | 6 | 60 | 14 |  |  | 120.7 |  | F2 | no of ligting |  |  |  |  | 10 | SAPRE |  | #VALUE! | #VALUE!
|  |  | 7 | 95 | 15 |  |  | 159.9 |  | 1.9 | H OF FLOOR-2 |  |  |  |  | 11 | 7 |  | 1400 | 7
|  |  | 8 | 67 | 9 |  |  | 106.7 | [7 empty] | 12 | 1 | 3 | 800 | 4
|  |  | 9 | 56 | 9 |  |  | 95.7 | [7 empty] | 13 | 7 |  | 1400 | 7
|  |  | 10 | 50 | 8 |  |  | 85.5 | [7 empty] | 14 | 7 |  | 1400 | 7
|  |  | 11 | 70 |  |  |  | 71.9 | [7 empty] | 15 | 1 | 5 | 1200 | 6
|  |  | 12 | 65 | 12 |  |  | 117.3 | [7 empty] | 16 | 1 | 5 | 1200 | 6
[16 empty] | 17 |  | 5 | 1000 | 5
[16 empty] | 18 | 2 | 2 | 800 | 4
[16 empty] | 19 |  | 6 | 1200 | 6
|  |  | POWER | [12 empty] | 20 | 4 | 2 | 1200 | 6
[16 empty] | 21 | 7 |  | 1400 | 7
[16 empty] | 22 | 1 | 4 | 1000 | 5
|  |  | NO OF CIR | F1 | F2 |  |  | TOTAL | [7 empty] | 23 | 1 | 3 | 800 | 4
|  |  | 13 | 36 | 4 |  |  | 59.4 | [7 empty] | 24 | 1 | 3 | 800 | 4
|  |  | 14 | 28 | 4 |  |  | 51.4 | [7 empty] | 25 | 3 | 2 | 1000 | 5
|  |  | 15 | 54 | 7 |  |  | 100.2 |  | F1 | LENGTH(in between + from panel) |  |  |  |  | 26 | 1 | 3 | 800 | 4
|  |  | 16 | 20 | 1 |  |  | 20.6 |  | F2 | no of SOCKETS |  |  |  |  | 27 |  | 5 | 1000 | 5
|  |  | 17 | 10 | 1 |  |  | 10.6 | [7 empty] | 28 |  | 5 | 1000 | 5
|  |  | 18 | 57 | 4 |  |  | 80.4 | [7 empty] | 29 | 2 | 4 | 1200 | 6
|  |  | 19 | 42 | 4 |  |  | 65.4 | [7 empty] | 30 | 1 | 2 | 600 | 3
|  |  | 20 | 49 | 6 |  |  | 87.6 | [7 empty] | 31 | 7 |  | 1400 | 7
|  |  | 21 | 47 | 4 |  |  | 70.4 | [7 empty] | 32 | 2 |  | 400 | 2
|  |  | 22 | 68 | 2 |  |  | 76.2 | [7 empty] | 33 | 4 | 2 | 1200 | 6
|  |  | 23 | 67 | 4 |  |  | 90.4 | [7 empty] | 34 | 4 | 2 | 1200 | 6
|  |  | 24 | 75 | 5 |  |  | 106 | [7 empty] | 35 | 2 | 4 | 1200 | 6
|  |  | 25 | 70 | 2 |  |  | 78.2 | [7 empty] | 36 | 4 |  | 800 | 4
[16 empty] | 37 | 4 | 1 | 1000 | 5
|  |  | total length from panel equal 250 m & average lenghth equal 20 m total length (in between and from panel) equal 630m & average 49 m | [12 empty] | 38 | 6 | 1 | 1400 | 7
[16 empty] | 39 | 4 | 2 | 1200 | 6
[16 empty] | 40 | 7 |  | 1400 | 7
[16 empty] | 41 | 8 |  | 1600 | 8
[16 empty] | 42 | 7 |  | 1400 | 7
[16 empty] | 43 | 7 |  | 1400 | 7
|  |  | HVAC | [12 empty] | 44 | 6 | 1 | 1400 | 7
[16 empty] | 45 | 4 | 1 | 1000 | 5
[16 empty] | 46 | 4 | 2 | 1200 | 6
|  |  | NO OF CIR | F1 |  |  |  | TOTAL | [7 empty] | 47 | 6 |  | 1200 | 6
|  |  | 26 | 62 |  |  |  | 63.9 | [7 empty] | 48 | 6 | 2 | 1600 | 8
|  |  | 27 | 47 |  |  |  | 48.9 | [7 empty] | 49 | 2 | 4 | 1200 | 6
|  |  | 28 | 48 |  |  |  | 49.9 | [7 empty] | 50 | 4 | 2 | 1200 | 6
|  |  | 29 | 42 |  |  |  | 43.9 |  | F1 | LENGTH(in between + from panel) |  |  |  |  | 51 | 1 | 2 | 600 | 3
|  |  | 30 | 41 |  |  |  | 42.9 |  | 1.9 | H OF FLOOR-2 |  |  |  |  | 52 | 6 | 2 | 1600 | 8
|  |  | 31 | 31 |  |  |  | 32.9 | [7 empty] | 53 | 2 | 2 | 800 | 4
|  |  | 32 | 23 |  |  |  | 24.9 | [7 empty] | 54 | 1 | 4 | 1000 | 5
|  |  | 33 | 34 |  |  |  | 35.9 | [7 empty] | 55 | 1 | 4 | 1000 | 5
|  |  | 34 | 21 |  |  |  | 22.9
|  |  | 35 | 29 |  |  |  | 30.9
|  |  | 36 | 13 |  |  |  | 14.9
total length from panel equal 300 m & average equal 27 m total length(in between and from panel)equal 390 m & average 36 m
in case of single phase
%𝑉.𝐷=((2∗𝑅∗𝐼∗𝐿)∗100)/((𝑉)∗1000)→ ((<2%))
in case of single phase
in case of three phase
%𝑉.𝐷=((√3∗𝑅∗𝐼∗𝐿)∗100)/((𝑉)∗1000)→((<3%))
in case of three phase
A(t)=A1+A2+A3+... where : A1 -1 cable in pipe A2- 2 cable in pipe A3-3cable in pipe
A(T)= total C.S.A of cableinside pipe D=outside dimmeter of cable from catalogue
max occupancy ratio :1C=53%fill , 2C=31%fill 3C+=40%fill
𝐹.𝑅=(𝐶.𝑆.𝐴 𝑜𝑓 𝑐𝑎𝑏𝑙𝑒𝑠)/(𝐶.𝑆.𝐴 𝑜𝑓 𝑝𝑖𝑝𝑒)∗100=𝐴(𝑡)/(𝐶.𝑆.𝐴 𝑜𝑓 𝑝𝑖𝑝𝑒)((<53%→1𝐶<31%→2𝐶<40%→+3𝐶))
A(t)=A1+A2+A3+... 𝐴=(𝜋/4) 𝐷^(2 )=0.79𝐷^(2 ) where : A1 -1 cable in pipe A2- 2 cable in pipe A3-3cable in pipe
A(T)= total C.S.A of cableinside pipe D=outside dimmeter of cable from catalogue
max occupancy ratio :1C=53%fill , 2C=31%fill 3C+=40%fill

## Sheet1
conductor | R-ohm/km
3X3mm | 7.66
3X6mm | 3.93
3X4mm | 5.88